## SkYSPark Data_w Will's Data
SkySpark + Will's Data | [11 empty] | EUI Monthly |  |  |  | EUI annual | [8 empty] | Outliers
Timestamp | Month | Building Name | Campus Center | Area | Building Use Type | Electricity 1 (kWh) | Electricity 2 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Suburban Propane: Corp Yard (1644-002486) Usage | Electric EUI(kBtu/sq.ft) | Gas EUI(kBtu/sq.ft) | Steam EUI(kBtu/sq.ft) | Chilled Water EUI(kBtu/sq.ft) | Electric EUI(kBtu/sq.ft) | Gas EUI(kBtu/sq.ft) | Steam EUI(kBtu/sq.ft) | Chilled Water EUI(kBtu/sq.ft) | Propane EUI(kBtu/sq.ft) | Total EUI(kBtu/sq.ft) | List of meter names | Questions | Notes | Electricity Outlier | Steam Outlier | CHW Outlier | District Electricity (Yes or No) | Incomplete | 2018 CHW? |  | Electricity 2 (kWh)_cost | Gas (therm)_cost | AS: Well Water (M) - Archived Usage - Archived | ATM PG&E SMD: ATM Electric (0161691543 / 0161691654) Usage | SJSU Main Campus Solar Duke Energy PPA (DER: 3802433) Cost | SJSU Main Campus Solar Duke Energy PPA (DER: 3802433) Usage | SJSU South Campus Solar Duke Energy PPA (DER: 3802432) Cost | SJSU South Campus Solar Duke Energy PPA (DER: 3802432) Usage | Stadium: East Side Electric (Closed) (PG&E: 4147571902-1 / 4145909668) Cost | Stadium: East Side Electric (Closed) (PG&E: 4147571902-1 / 4145909668) Usage | Stadium: South Scoreboard Electric (PG&E: 4147571902-1 / 7870442434) Cost | Stadium: South Scoreboard Electric (PG&E: 4147571902-1 / 7870442434) Usage | SC: CEFCU Stadium PG&E SMD: Stadium Concession Stand Electric (4147571902 / 4146304770) Usage | SC: CEFCU Stadium PG&E SMD: Stadium East Side Electric (4147571902 / 4145909668) Usage | SC: CEFCU Stadium PG&E SMD: Stadium South Scoreboard Electric (4147571902 / 7870442434) Usage | SC: CEFCU Stadium PG&E SMD: West Main Gate Electric (4147571902 / 4140791751) Usage | SC: CEFCU Stadium PG&E SMD: West Ticket Booth + Stadium Light Electric (4147571902 / 4144777738) Usage | West Ticket Booth + Stadium Light Electric (PG&E: 4147571902-1 / 4146948395) Cost | West Ticket Booth + Stadium Light Electric (PG&E: 4147571902-1 / 4146948395) Usage | CDC: Elec (PG&E: 8588879680-3 / 8588879609) Cost | SC: Concessions PG&E SMD: Parking Electric (2912101405 / 2912101607) Usage | Suburban Propane: Corp Yard (1644-002486) Cost | MLK: CHW Meter (M) Usage (Archived) | MLK: Steam Meter (M) Usage (Archived 2015-2021) | Duncan Electric Meter (N4) Usage | Duncan Hall: Electricity 2 (M) Usage | Eng Electric Meter (N4) Usage | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Cost | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Usage | SC: Field House PG&E SMD: Athletic Module Electric (4147571902 / 4149254333) Usage | SC: Field House PG&E SMD: Field House Electric (4147571902 / 4146143451) Usage | Golf Complex PG&E SMD: Golf Electric (4147571902 / 4148940516) Usage | HT: Aux Fire Pump Elec (PG&E: 6290092604-9 / 6290092893) Cost | HT: Aux Fire Pump Elec (PG&E: 6290092604-9 / 6290092893) Usage | HT: Elec Total (C) Cost (C) | HT: Elec Total (C) Usage (C) | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Cost | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Usage | OFF: Hammer Theater PG&E SMD: HT Gas (6290092604 / 6290092347) Usage | OFF: Hammer Theater PG&E SMD: HT Main Electric (6290092604 / 6290092168) Usage | HGH CHW Meter (N4) Usage | HGH Electric Meter (N4) Usage | HGH Steam Meter (N4) Usage | MacQuarrie Hall: Steam (M) Usage.1 | MQH: CHW-78-1-2 (M) Usage - Archived | MQH: CHW-78-2-2 (M) Usage | MQH: CHW Meter (N4) Usage | MQH: Elec Old AS House ISB Temp 1 (M) Usage | MQH: Elec Spartan Shops (M) Usage | MQH: Elec SWB PC-1 (M) Usage - Archived | MQH: Elec Total (C) Usage | MQH: Electric Meter (N4) Usage | MQH: Steam Meter (M) Usage - Archived | MQH: Steam Meter (N4) Usage | MLML: Pump House Elec (PG&E: 1003320516-1 / 1003320595) Cost | MLML: Pump House Elec (PG&E: 1003320516-1 / 1003320595) Usage | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Cost | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Usage | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Cost | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Usage | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Cost | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Usage | MLML: Small Boats Electric (PG&E: 5130218023-0 / 5130218783) Cost | MLML: Small Boats Electric (PG&E: 5130218023-0 / 5130218783) Usage | MLML: Small Boats Gas (PG&E: 7963846344-2 / 7963846005) Cost | MLML: Small Boats Gas (PG&E: 7963846344-2 / 7963846005) Usage | OFF: Marine Lab PG&E SMD: MLML Main Electric (9928867424 / 9928500055) Usage | OFF: Marine Lab PG&E SMD: MLML Main Gas (4348987890 / 4348987005) Usage | OFF: Marine Lab PG&E SMD: MLML Pump House Elec (1003320516 / 1003320595) Usage | OFF: Marine Lab PG&E SMD: MLML Sea Lion Elec A (4269991711 / 4269991931) Usage | Music: South Steam (Bamboo Grove) (M) Usage - Archived | Music: Steam 1 (M) Usage | Music: Steam 2 (M) Usage | Music 1 CHW Meter (N4) Usage | Music 1 Electric Meter (N4) Usage | Music 1 Steam Meter (N4) Usage | Music 2 CHW Meter (N4) Usage | Music 2 Electric Meter (N4) Usage | Music 2 Steam Meter (N4) Usage | SC: Physical Ed PG&E SMD: Marching Band Field Electric (4147571902 / 7953776421) Usage | SC: Physical Ed PG&E SMD: Softball/Tennis/Batting Cages Electric (4147571902 / 4143162076) Usage | EVC: Chilled Water Usage (M) | EVC: Chilled Water Usage (M) - Archived (2013-2015) | EVC: Chilled Water Usage (M) - Archived (2015-2021) | EVC: Steam (M) Usage - Estimate | SC: Simpkins Athletic PG&E SMD: Import Simpkins Athletic Electric (4147571902 / 4147571157) Usage | SRAC CHW (M) Usage | SPXEast: Steam (M) Usage - Archived | SPX East Electric Meter (N4) Usage | SPX East Steam Meter (N4) Usage | SCC: Ramp Lighting (M) Usage | Student Services PG&E SMD: SSC Gas (9817802206 / 9817802005) Usage | SWC: CHW (M) Usage | SH: CHW Mech Rm 128 Usage - Archived | SH: CHW Rm 122 Usage - Archived | SH: Elec Rm 122 Usage - Archived | SH: Steam Rm 122 Usage (M) | SH: Steam Rm 122 Usage (M) - Archived (Feb 20-Nov 21) | Sweeney Hall: Chilled Water 2 (M) Usage | Sweeney Hall CHW Meter (N4) Usage | Sweeney Hall Electric Meter (N4) Usage | Sweeney Hall Steam Meter (N4) Usage | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Cost | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Usage | WSH: NatGas (PG&E: 4564269832-3 / 4564269015) Usage | WSH: Elec (M) Usage - Archived | YUH: CHW (M) Usage - Archived | YUH: Elec (M) Usage - Archived | YUH: Steam (M) Usage - Archived | Uchida Hall CHW Meter (N4) Usage | Uchida Hall Electric Meter (N4) Usage | Uchida Hall Steam Meter (N4) Usage
2023-01-01 | 1 | Administration | Main campus | 39323 | Office | 58 | [5 empty] | 0.0050326 | 0 | 0 | 0 | 0.053231 |  |  |  |  | 0.053231 | Admin: Electricity (M) Usage - Archived |  |  | FALSE | TRUE | TRUE | Y | S,C
2023-02-01 | 2 | Administration | Main campus | 39323 | Office | 57 | [5 empty] | 0.0049458 | 0 | 0 | 0 | [6 empty] | Steam usage data was missing and has been calculated based on metered data |  |  | FALSE | TRUE | TRUE | Y
2023-03-01 | 3 | Administration | Main campus | 39323 | Office | 57 | [5 empty] | 0.0049458 | 0 | 0 | 0 | [6 empty] | Chilled Water usage data was missing and has been calculated based on metered data |  |  | FALSE | TRUE | TRUE | Y
2023-04-01 | 4 | Administration | Main campus | 39323 | Office | 49 | [5 empty] | 0.0042517 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-05-01 | 5 | Administration | Main campus | 39323 | Office | 46 | [5 empty] | 0.0039914 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-06-01 | 6 | Administration | Main campus | 39323 | Office | 46 | [5 empty] | 0.0039914 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-07-01 | 7 | Administration | Main campus | 39323 | Office | 51 | [5 empty] | 0.0044252 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-08-01 | 8 | Administration | Main campus | 39323 | Office | 48 | [5 empty] | 0.0041649 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-09-01 | 9 | Administration | Main campus | 39323 | Office | 47 | [5 empty] | 0.0040781 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-10-01 | 10 | Administration | Main campus | 39323 | Office | 54 | [5 empty] | 0.0046855 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-11-01 | 11 | Administration | Main campus | 39323 | Office | 59 | [5 empty] | 0.0051193 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-12-01 | 12 | Administration | Main campus | 39323 | Office | 41.4801 | [5 empty] | 0.0035992 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-01-01 | 1 | Art | Main campus | 85419 | Lab | 102535.931 |  | 0 | 7115.621 | 12217.2819 |  | 4.0957 | 0 | 8.3303 | 1.7163 | 37.9257 | 0.0061174 | 47.2631 | 20.7447 |  | 105.9395 | Art : Electricity (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Art | Main campus | 85419 | Lab | 101147 |  | 0 | 6500.3516 | 11536.3224 |  | 4.0402 | 0 | 7.61 | 1.6207 | [6 empty] | Art PG&E SMD: Art Gas (4713751639 / 4713751005) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Art | Main campus | 85419 | Lab | 107805.3015 |  | 0 | 7061.428 | 13805.6848 |  | 4.3062 | 0 | 8.2668 | 1.9395 | [6 empty] | Art : Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Art | Main campus | 85419 | Lab | 104656.6985 |  | 1.0425 | 5075.2126 | 15674.6627 |  | 4.1804 | 0.0012204 | 5.9416 | 2.202 | [6 empty] | Art : Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Art | Main campus | 85419 | Lab | 104333 |  | 0 | 3585.1172 | 16223.3908 |  | 4.1675 | 0 | 4.1971 | 2.2791 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Art | Main campus | 85419 | Lab | 76884.5714 |  | 0 | 1761.0603 | 13605.4128 |  | 3.0711 | 0 | 2.0617 | 1.9113 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Art | Main campus | 85419 | Lab | 70571.4286 |  | 0 | 1209.0179 | 15184.7767 |  | 2.8189 | 0 | 1.4154 | 2.1332 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Art | Main campus | 85419 | Lab | 55735.5571 |  | 1.0485 | 658.1964 | 13469.9876 |  | 2.2263 | 0.0012275 | 0.77055 | 1.8923 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Art | Main campus | 85419 | Lab | 57098.5143 |  | 0 | 1186.519 | 14247.9617 |  | 2.2808 | 0 | 1.3891 | 2.0016 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Art | Main campus | 85419 | Lab | 62380.4286 |  | 1.0394 | 1652.0815 | 15026.5973 |  | 2.4917 | 0.0012168 | 1.9341 | 2.111 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Art | Main campus | 85419 | Lab | 57216.3581 |  | 1.0455 | 2161.21 | 5086.183 |  | 2.2855 | 0.001224 | 2.5301 | 0.71453 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Art | Main campus | 85419 | Lab | 49099.3315 |  | 1.0496 | 2405.8105 | 1587.6335 |  | 1.9612 | 0.0012287 | 2.8165 | 0.22304 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Art Foundry | Art Foundry | 7934 | Storage | 3966.5323 |  | 498.329 |  |  |  | 1.7058 | 6.2809 | 0 | 0 | 23.7748 | 47.3396 |  |  |  | 71.1144 | Art Foundry: Electric (PG&E: 5463751591-4 / 5469494524) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 1.6909 | 1.6723
2023-02-01 | 2 | Art Foundry | Art Foundry | 7934 | Storage | 3921.313 |  | 686.271 |  |  |  | 1.6864 | 8.6497 | 0 | 0 | [6 empty] | Art Foundry: Gas (PG&E: 5317852558-9 / 5317852005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 1.869 | 2.4885
2023-03-01 | 3 | Art Foundry | Art Foundry | 7934 | Storage | 5039.4881 |  | 1198.4633 |  |  |  | 2.1672 | 15.1054 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.2161 | 3.0538
2023-04-01 | 4 | Art Foundry | Art Foundry | 7934 | Storage | 5100.3229 |  | 354.0117 |  |  |  | 2.1934 | 4.462 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.3275 | 0.7861
2023-05-01 | 5 | Art Foundry | Art Foundry | 7934 | Storage | 5033.005 |  | 100.3831 |  |  |  | 2.1644 | 1.2652 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.2628 | 0.22459
2023-06-01 | 6 | Art Foundry | Art Foundry | 7934 | Storage | 4577.4181 |  | 26.129 |  |  |  | 1.9685 | 0.32933 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.3159 | 0.10976
2023-07-01 | 7 | Art Foundry | Art Foundry | 7934 | Storage | 5602.0297 |  | 12.9032 |  |  |  | 2.4091 | 0.16263 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.8838 | 0.09031
2023-08-01 | 8 | Art Foundry | Art Foundry | 7934 | Storage | 6189.0656 |  | 5.1097 |  |  |  | 2.6616 | 0.064402 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.2061 | 0.078301
2023-09-01 | 9 | Art Foundry | Art Foundry | 7934 | Storage | 5033.34 |  | 63.8 |  |  |  | 2.1646 | 0.80413 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.6886 | 0.2002
2023-10-01 | 10 | Art Foundry | Art Foundry | 7934 | Storage | 4253.5917 |  | 102.3465 |  |  |  | 1.8292 | 1.29 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.049 | 0.29301
2023-11-01 | 11 | Art Foundry | Art Foundry | 7934 | Storage | 3787.004 |  | 411.8084 |  |  |  | 1.6286 | 5.1904 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.8507 | 1.135
2023-12-01 | 12 | Art Foundry | Art Foundry | 7934 | Storage | 2781.0176 |  | 296.3693 |  |  |  | 1.196 | 3.7354 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.3595 | 0.86429
2022-01-01 | 1 | Associated Students House | Main campus | 8591 | Office | 3811.8788 | [5 empty] | 1.5139 | 0 | 0 | 0 | 15.3777 |  |  |  |  | 15.3777 | AS House New Electric (M) Usage |  |  | FALSE | TRUE | TRUE | Y
2022-02-01 | 2 | Associated Students House | Main campus | 8591 | Office | 3358 | [5 empty] | 1.3337 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-03-01 | 3 | Associated Students House | Main campus | 8591 | Office | 3000 | [5 empty] | 1.1915 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-04-01 | 4 | Associated Students House | Main campus | 8591 | Office | 2666.129 | [5 empty] | 1.0589 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-05-01 | 5 | Associated Students House | Main campus | 8591 | Office | 2764.871 | [5 empty] | 1.0981 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-06-01 | 6 | Associated Students House | Main campus | 8591 | Office | 3294 | [5 empty] | 1.3082 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-07-01 | 7 | Associated Students House | Main campus | 8591 | Office | 3048.6562 | [5 empty] | 1.2108 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-08-01 | 8 | Associated Students House | Main campus | 8591 | Office | 3280.3437 | [5 empty] | 1.3028 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-09-01 | 9 | Associated Students House | Main campus | 8591 | Office | 3361 | [5 empty] | 1.3349 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-10-01 | 10 | Associated Students House | Main campus | 8591 | Office | 2996 | [5 empty] | 1.1899 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-11-01 | 11 | Associated Students House | Main campus | 8591 | Office | 3347 | [5 empty] | 1.3293 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2022-12-01 | 12 | Associated Students House | Main campus | 8591 | Office | 3791.3939 | [5 empty] | 1.5058 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-01-01 | 1 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2317.8417 | [5 empty] | 5.6651 | 0 | 0 | 0 | 70.9973 |  |  |  |  | 70.9973 | ATM: Electric (PG&E: 0161691543-3 / 0161691654) Usage | Two solar electric meters -- are they for solar generation from this building? |  | FALSE | TRUE | TRUE | N |  |  |  | 0.98253 |  |  | 1419.425 | 10.9839 | 94693 | 6.7859 | 38393
2023-02-01 | 2 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2018.4357 | [5 empty] | 4.9333 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 0.91265 |  |  | 1943.5387 | 15.4093 | 119989 | 9.3766 | 47917
2023-03-01 | 3 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2246.3136 | [5 empty] | 5.4903 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 0.97849 |  |  | 2252.1961 | 18.7478 | 161409 | 11.663 | 65898
2023-04-01 | 4 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2223.0582 | [5 empty] | 5.4334 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.0149 |  |  | 2198.5817 | 29.5236 | 247174 | 18.3354 | 100621
2023-05-01 | 5 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2442.2334 | [5 empty] | 5.9691 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.0941 |  |  | 2377.3857 | 28.0879 | 242148 | 18.182 | 102870
2023-06-01 | 6 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2448.5576 | [5 empty] | 5.9846 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.2191 |  |  | 2439.4816 | 31.8078 | 265372 | 20.3186 | 111250
2023-07-01 | 7 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2561.0641 | [5 empty] | 6.2596 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.2955 |  |  | 2568.0753 | 33.5112 | 288903 | 20.4055 | 115450
2023-08-01 | 8 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2773.5055 | [5 empty] | 6.7788 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.4209 |  |  | 2885.5756 | 28.5943 | 246514 | 16.2745 | 92078
2023-09-01 | 9 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2577.4935 | [5 empty] | 6.2997 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.3179 |  |  | 2523.9794 | 21.7277 | 181905.6 | 11.7223 | 64183
2023-10-01 | 10 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2598.4789 | [5 empty] | 6.351 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.2293 |  |  | 2611.4166 | 18.5516 | 159935 | 10.7885 | 61039
2023-11-01 | 11 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2441.6589 | [5 empty] | 5.9677 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.184 |  |  | 2445.3049 | 11.7311 | 98008 | 7.776 | 42635
2023-12-01 | 12 | Automated Bank Teller Facility | Main campus | 1396 | Office | 2399.4851 | [5 empty] | 5.8646 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 1.1607 |  |  | 2409.1359 | 9.9906 | 86130 | 5.4908 | 31066
2023-01-01 | 1 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 103699.569 |  |  | 9803.2085 | 1689.6605 |  | 2.5714 | 0 | 7.1244 | 0.14735 | 32.4289 |  | 52.0877 | 21.0876 |  | 105.6041 | Boccardo Business: Electricity (M) Usage |  | Summed areas -BBC,BT, there is a food tenant in the electric meter but electric usage is very little so it has not been separated | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 96736.5 |  |  | 8322.1094 | 6833.06 |  | 2.3987 | 0 | 6.048 | 0.5959 | [6 empty] | Boccardo Business: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 105933.4121 |  |  | 9215.7303 | 1019.9991 |  | 2.6268 | 0 | 6.6974 | 0.088953 | [6 empty] | Boccardo Business: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 107979.5879 |  |  | 4037.8635 | 4961.0442 |  | 2.6775 | 0 | 2.9345 | 0.43265 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 116107 |  |  | 6455.7031 | 5698.0143 |  | 2.879 | 0 | 4.6916 | 0.49692 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 120264.4634 |  |  | 6693.064 | 22904.9527 |  | 2.9821 | 0 | 4.8641 | 1.9975 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 120514.5366 |  |  | 6492.6391 | 51267.2105 |  | 2.9883 | 0 | 4.7185 | 4.4709 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 114224 |  |  | 2586.4241 | 58428.8569 |  | 2.8323 | 0 | 1.8797 | 5.0955 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 114124.963 |  |  | 1156.9902 | 41662.8423 |  | 2.8299 | 0 | 0.84083 | 3.6334 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 112149.037 |  |  | 3717.9138 | 37645.4668 |  | 2.7809 | 0 | 2.702 | 3.283 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 99933.8392 |  |  | 5359.9798 | 6787.2498 |  | 2.478 | 0 | 3.8953 | 0.59191 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Boccardo Business Classroom Building +Business Tower | Main campus | 137601 | Academic | 96143.6263 |  |  | 7831.5477 | 2907.3101 |  | 2.384 | 0 | 5.6915 | 0.25354 | [9 empty] | FALSE | FALSE | FALSE | Y
2021-01-01 | 1 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 134.2 | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | Jazzland: Coffee Conces. (BT) (M) Usage - Archived |  |  | TRUE | TRUE | TRUE | Y |  |  | Will to confirm if BT Jazzland is included in BBC or not
2021-02-01 | 2 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 999.9999 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-03-01 | 3 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 715.8 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-04-01 | 4 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 428 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-05-01 | 5 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 491 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-06-01 | 6 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 191 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-07-01 | 7 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 368 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-08-01 | 8 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 344 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-09-01 | 9 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 424 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-10-01 | 10 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 589 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-11-01 | 11 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 458 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2021-12-01 | 12 | Business Tower-Jazzland Tenant | Main campus |  | Food Service | 938 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-01-01 | 1 | Campus Village 1 | Main campus | 960662 | Residential | 365132.591 |  |  | 37563 | 26803 |  | 1.2968 | 0 | 3.9101 | 0.33481 | 15.7982 |  | 23.889 | 10.3943 |  | 50.0816 | CV1: Steam Estimate (M) Usage |  | Summed areas -CV A,B,C,Garage | FALSE | FALSE | FALSE | Y |  |  | campus gaage included in elec usage, to be subtractwed and area bacl to just three
2023-02-01 | 2 | Campus Village 1 | Main campus | 960662 | Residential | 356083.4512 |  |  | 35963 | 39259 |  | 1.2647 | 0 | 3.7436 | 0.4904 | [6 empty] | CV1: CHW Estimate (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Campus Village 1 | Main campus | 960662 | Residential | 377928.5929 |  |  | 28489 | 57813 |  | 1.3423 | 0 | 2.9656 | 0.72216 | [6 empty] | Will's calculated electric feeder data minus Market electric minus garage use |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Campus Village 1 | Main campus | 960662 | Residential | 409551.7882 |  |  | 30032 | 53645 |  | 1.4546 | 0 | 3.1262 | 0.6701 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Campus Village 1 | Main campus | 960662 | Residential | 402231.0613 |  |  | 1557 | 84490 |  | 1.4286 | 0 | 0.16208 | 1.0554 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Campus Village 1 | Main campus | 960662 | Residential | 218147.318 |  |  | 1155 | 91714 |  | 0.7748 | 0 | 0.12023 | 1.1456 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Campus Village 1 | Main campus | 960662 | Residential | 319954.1863 |  |  | 1189 | 121752 |  | 1.1364 | 0 | 0.12377 | 1.5209 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Campus Village 1 | Main campus | 960662 | Residential | 358366.5288 |  |  | 1204 | 112109 |  | 1.2728 | 0 | 0.12533 | 1.4004 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Campus Village 1 | Main campus | 960662 | Residential | 416098.2529 |  |  | 13996 | 88372 |  | 1.4779 | 0 | 1.4569 | 1.1039 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Campus Village 1 | Main campus | 960662 | Residential | 439122.0046 |  |  | 21031 | 77881 |  | 1.5596 | 0 | 2.1892 | 0.97284 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Campus Village 1 | Main campus | 960662 | Residential | 403710.4624 |  |  | 24095 | 43205 |  | 1.4339 | 0 | 2.5082 | 0.53969 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Campus Village 1 | Main campus | 960662 | Residential | 381723.4807 |  |  | 33219 | 35076 |  | 1.3558 | 0 | 3.4579 | 0.43815 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Campus Village A-Food Tenant | Main campus |  |  | 10458.9091 | [5 empty] | 0 | 0 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! | Campus Village A CV1: Market Electric Meter (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-02-01 | 2 | Campus Village A-Food Tenant | Main campus |  |  | 13945 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-03-01 | 3 | Campus Village A-Food Tenant | Main campus |  |  | 13020.8167 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-04-01 | 4 | Campus Village A-Food Tenant | Main campus |  |  | 14584.1833 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-05-01 | 5 | Campus Village A-Food Tenant | Main campus |  |  | 13604 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-06-01 | 6 | Campus Village A-Food Tenant | Main campus |  |  | 8669.1429 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-07-01 | 7 | Campus Village A-Food Tenant | Main campus |  |  | 9065.8571 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-08-01 | 8 | Campus Village A-Food Tenant | Main campus |  |  | 13082 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-09-01 | 9 | Campus Village A-Food Tenant | Main campus |  |  | 15325 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-10-01 | 10 | Campus Village A-Food Tenant | Main campus |  |  | 15584 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-11-01 | 11 | Campus Village A-Food Tenant | Main campus |  |  | 12983.4552 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-12-01 | 12 | Campus Village A-Food Tenant | Main campus |  |  | 10577.0965 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-01-01 | 1 | Campus Village Phase 2 | Main campus | 186318 | Residential | 83762.9394 |  |  | 11923.3333 | 3923.6859 |  | 1.5339 | 0 | 6.3995 | 0.25271 | 20.7839 |  | 44.0611 | 15.9259 |  | 80.7709 | CV2: Electric (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Campus Village Phase 2 | Main campus | 186318 | Residential | 97842 |  |  | 12280 | 8169.0943 |  | 1.7918 | 0 | 6.5909 | 0.52614 | [6 empty] | CV2: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Campus Village Phase 2 | Main campus | 186318 | Residential | 103142.6776 |  |  | 12060.8344 | 9228.1118 |  | 1.8888 | 0 | 6.4733 | 0.59435 | [6 empty] | CV2: CHW (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Campus Village Phase 2 | Main campus | 186318 | Residential | 106302.3224 |  |  | 8269.1656 | 17378.1035 |  | 1.9467 | 0 | 4.4382 | 1.1193 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Campus Village Phase 2 | Main campus | 186318 | Residential | 96875 |  |  | 5990 | 17364.9588 |  | 1.7741 | 0 | 3.2149 | 1.1184 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Campus Village Phase 2 | Main campus | 186318 | Residential | 70182.8571 |  |  | 3394.2857 | 17248.8873 |  | 1.2852 | 0 | 1.8218 | 1.1109 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Campus Village Phase 2 | Main campus | 186318 | Residential | 75508.1429 |  |  | 2435.7143 | 30211.369 |  | 1.3828 | 0 | 1.3073 | 1.9458 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Campus Village Phase 2 | Main campus | 186318 | Residential | 92632.4286 |  |  | 1550 | 46773.1336 |  | 1.6964 | 0 | 0.83191 | 3.0125 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Campus Village Phase 2 | Main campus | 186318 | Residential | 105804.6786 |  |  | 2985.7143 | 37017.1661 |  | 1.9376 | 0 | 1.6025 | 2.3841 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Campus Village Phase 2 | Main campus | 186318 | Residential | 112315.8929 |  |  | 4154.2857 | 36016.9014 |  | 2.0568 | 0 | 2.2297 | 2.3197 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Campus Village Phase 2 | Main campus | 186318 | Residential | 104591.8241 |  |  | 7619.1425 | 15659.3276 |  | 1.9154 | 0 | 4.0893 | 1.0086 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Campus Village Phase 2 | Main campus | 186318 | Residential | 85979.0207 |  |  | 9431.2023 | 8283.1558 |  | 1.5745 | 0 | 5.0619 | 0.53349 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 33373.0514 | [5 empty] | 9.8665 | 0 | 0 | 0 | 165.4498 |  |  |  |  | 165.4498 | SC: CEFCU Stadium PG&E SMD: Stadium Concession Stand Electric (4147571902 / 4146304770) Usage | Is it correct to combine all electric meters( two are from 2018) | Negative | FALSE | TRUE | TRUE |  | G |  | Solar to be added | 1.546 | [16 empty] | 3.4269 | 4433.2527
2023-02-01 | 2 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 58734.0845 | [5 empty] | 17.3642 | 0 | 0 | 0 | [6 empty] | SC: CEFCU Stadium PG&E SMD: Stadium South Scoreboard Electric (4147571902 / 7870442434) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 2.9593 | [16 empty] | 4.2035 | 7377.714
2023-03-01 | 3 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 52268.2408 | [5 empty] | 15.4527 | 0 | 0 | 0 | [6 empty] | SC: CEFCU Stadium PG&E SMD: West Main Gate Electric (4147571902 / 4140791751) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 1.7933 | [16 empty] | 4.4224 | 6828.8379
2023-04-01 | 4 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 49176.7535 | [5 empty] | 14.5387 | 0 | 0 | 0 | [6 empty] | SC: CEFCU Stadium PG&E SMD: West Ticket Booth + Stadium Light Electric (4147571902 / 4144777738) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 1.1197 | [16 empty] | 3.5327 | -570.9712
2023-05-01 | 5 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 43333.8242 | [5 empty] | 12.8113 | 0 | 0 | 0 | [6 empty] | 2018 :SC: CEFCU Stadium PG&E SMD: No. Main Gate Electric (4147571902 / 6595532772) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.97053 | [16 empty] | 0.83594 | -6701.9032
2023-06-01 | 6 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 46863.8859 | [5 empty] | 13.8549 | 0 | 0 | 0 | [6 empty] | 2018: SC: CEFCU Stadium PG&E SMD: Stadium East Side Electric (4147571902 / 4145909668) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.89414 | [16 empty] | 1.5058 | -6766.7843
2023-07-01 | 7 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 48633.1293 | [5 empty] | 14.378 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.3353 | [16 empty] | 2.485 | -4099.9332
2023-08-01 | 8 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 56756.2161 | [5 empty] | 16.7795 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.3526 | [16 empty] | 3.3413 | 3869.0207
2023-09-01 | 9 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 48667.4179 | [5 empty] | 14.3881 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.4762 | [16 empty] | 3.7394 | 5431.85
2023-10-01 | 10 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 48269.0335 | [5 empty] | 14.2703 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.3655 | [16 empty] | 3.8255 | 6215.806
2023-11-01 | 11 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 41400.3221 | [5 empty] | 12.2397 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.258 | [16 empty] | 4.0289 | 7770.2344
2023-12-01 | 12 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | 32153.5729 | [5 empty] | 9.5059 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.7334 | [16 empty] | 2.9391 | 4584.6129
2023-01-01 | 1 | Central Classroom Building | Main campus | 33407 | Academic | 22429.431 |  | 12.7062 | 797.5684 | 1408.6126 |  | 2.2908 | 0.038034 | 2.3874 | 0.50598 | 31.0078 | 0.80856 | 29.6447 | 41.7191 |  | 103.1802 | Central Classroom Bldg: Electricity (M) Usage |  | Gas for cooking only | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Central Classroom Building | Main campus | 33407 | Academic | 25594.5 |  | 21.13 | 875.5664 | 781.6256 |  | 2.6141 | 0.06325 | 2.6209 | 0.28076 | [6 empty] | Central Classroom Bldg PG&E SMD: CCB Gas (4838752674 / 4838752005) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Central Classroom Building | Main campus | 33407 | Academic | 27439.3375 |  | 24.0758 | 1054.4662 | 843.9606 |  | 2.8025 | 0.072068 | 3.1564 | 0.30316 | [6 empty] | Central Classroom Bldg: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Central Classroom Building | Main campus | 33407 | Academic | 27463.6625 |  | 27.1062 | 849.7525 | 5577.9017 |  | 2.805 | 0.081139 | 2.5436 | 2.0036 | [6 empty] | Central Classroom Bldg: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Central Classroom Building | Main campus | 33407 | Academic | 26857.5 |  | 23.008 | 877.1973 | 8922.9015 |  | 2.7431 | 0.068872 | 2.6258 | 3.2052 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Central Classroom Building | Main campus | 33407 | Academic | 23764.0244 |  | 19.8186 | 795.9675 | 14833.2719 |  | 2.4271 | 0.059325 | 2.3826 | 5.3282 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Central Classroom Building | Main campus | 33407 | Academic | 24717.4756 |  | 20.9606 | 644.9309 | 16982.3499 |  | 2.5245 | 0.062743 | 1.9305 | 6.1002 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Central Classroom Building | Main campus | 33407 | Academic | 24128.1857 |  | 21.059 | 582.2706 | 16814.6362 |  | 2.4643 | 0.063038 | 1.743 | 6.0399 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Central Classroom Building | Main campus | 33407 | Academic | 25513.2772 |  | 27.3458 | 743.2437 | 14955.5713 |  | 2.6058 | 0.081856 | 2.2248 | 5.3721 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Central Classroom Building | Main campus | 33407 | Academic | 26114.537 |  | 27.0112 | 743.3822 | 15094.4543 |  | 2.6672 | 0.080855 | 2.2252 | 5.422 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Central Classroom Building | Main campus | 33407 | Academic | 25032.2472 |  | 24.1063 | 982.4481 | 9242.1102 |  | 2.5567 | 0.072159 | 2.9408 | 3.3198 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Central Classroom Building | Main campus | 33407 | Academic | 24544.4425 |  | 21.7879 | 956.608 | 10685.0432 |  | 2.5068 | 0.065219 | 2.8635 | 3.8381 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Child Development Center | Main campus | 12889 | Academic | 2434.888 |  | 124.1939 |  |  |  | 0.64457 | 0.96357 | 0 | 0 | 10.0648 | 7.1905 |  |  |  | 17.2553 | CDC: Elec (PG&E: 8588879680-3 / 8588879609) Usage |  |  | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.41926 | [17 empty] | 1.0388
2023-02-01 | 2 | Child Development Center | Main campus | 12889 | Academic | 2802.1913 |  | 156.4954 |  |  |  | 0.7418 | 1.2142 | 0 | 0 | [6 empty] | CDC: Gas (PG&E: 8588879680-3 / 8588879977) Usage |  |  | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.58647 | [17 empty] | 1.3209
2023-03-01 | 3 | Child Development Center | Main campus | 12889 | Academic | 2705.1182 |  | 136.6212 |  |  |  | 0.7161 | 1.06 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.37002 | [17 empty] | 1.1832
2023-04-01 | 4 | Child Development Center | Main campus | 12889 | Academic | 2485.077 |  | 82.1638 |  |  |  | 0.65785 | 0.63747 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.17151 | [17 empty] | 1.1282
2023-05-01 | 5 | Child Development Center | Main campus | 12889 | Academic | 2952.3745 |  | 60.4894 |  |  |  | 0.78156 | 0.46931 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.11397 | [17 empty] | 1.3231
2023-06-01 | 6 | Child Development Center | Main campus | 12889 | Academic | 3149.441 |  | 41.0343 |  |  |  | 0.83373 | 0.31837 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.087673 | [17 empty] | 1.5718
2023-07-01 | 7 | Child Development Center | Main campus | 12889 | Academic | 4118.3941 |  | 18.2004 |  |  |  | 1.0902 | 0.14121 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.051824 | [17 empty] | 2.0742
2023-08-01 | 8 | Child Development Center | Main campus | 12889 | Academic | 5179.6239 |  | 31.0621 |  |  |  | 1.3712 | 0.241 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.07711 | [17 empty] | 2.6251
2023-09-01 | 9 | Child Development Center | Main campus | 12889 | Academic | 4087.5645 |  | 56.8 |  |  |  | 1.0821 | 0.44069 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.13546 | [17 empty] | 2.1283
2023-10-01 | 10 | Child Development Center | Main campus | 12889 | Academic | 3258.6877 |  | 60.4261 |  |  |  | 0.86265 | 0.46882 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.15379 | [17 empty] | 1.5589
2023-11-01 | 11 | Child Development Center | Main campus | 12889 | Academic | 2455.3438 |  | 69.3739 |  |  |  | 0.64998 | 0.53824 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.19901 | [17 empty] | 1.1932
2023-12-01 | 12 | Child Development Center | Main campus | 12889 | Academic | 2391.5324 |  | 89.9273 |  |  |  | 0.63309 | 0.69771 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.26812 | [17 empty] | 1.1785
2023-01-01 | 1 | Clark Hall | Main campus | 192428 | Academic | 72106.938 |  |  | 5989.0801 | 7866.6352 |  | 1.2786 | 0 | 3.1124 | 0.49057 | 13.875 |  | 17.7446 | 14.4301 |  | 46.0497 | Will's Manual Data- Electric 1 |  |  | FALSE | FALSE | FALSE | Y |  | Y | change chw to Wills data, units are an issue
2023-02-01 | 2 | Clark Hall | Main campus | 192428 | Academic | 42879.156 |  |  | 2621.0151 | 10766.6236 |  | 0.7603 | 0 | 1.3621 | 0.67142 | [6 empty] | Will's Manual Data- Electric 2 |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Clark Hall | Main campus | 192428 | Academic | 46676.156 |  |  | 2621.0151 | 10991.5381 |  | 0.82763 | 0 | 1.3621 | 0.68544 | [6 empty] | Will's Manual Data- Steam |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Clark Hall | Main campus | 192428 | Academic | 78455.375 |  |  | 3928.3913 | 13915.0628 |  | 1.3911 | 0 | 2.0415 | 0.86776 | [6 empty] | 2018 - CL: Chilled Water (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Clark Hall | Main campus | 192428 | Academic | 21041 |  |  |  | 12169.9682 |  | 0.37308 | 0 | 0 | 0.75893 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Clark Hall | Main campus | 192428 | Academic | 60724.101 |  |  |  | 16488.4443 |  | 1.0767 | 0 | 0 | 1.0282 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Clark Hall | Main campus | 192428 | Academic | 89848.156 |  |  | 1520.559 | 28015.6235 |  | 1.5931 | 0 | 0.7902 | 1.7471 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Clark Hall | Main campus | 192428 | Academic | 73592.625 |  |  | 1252.6851 | 55797.7319 |  | 1.3049 | 0 | 0.65099 | 3.4796 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Clark Hall | Main campus | 192428 | Academic | 83858.313 |  |  | 2025.2628 | 27420.7537 |  | 1.4869 | 0 | 1.0525 | 1.71 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Clark Hall | Main campus | 192428 | Academic | 82453.437 |  |  | 3627.9093 | 29264.8076 |  | 1.462 | 0 | 1.8853 | 1.825 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Clark Hall | Main campus | 192428 | Academic | 65173 |  |  | 5385.4295 | 12614.9834 |  | 1.1556 | 0 | 2.7987 | 0.78668 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Clark Hall | Main campus | 192428 | Academic | 65706.75 |  |  | 5174.3184 | 6083.7289 |  | 1.1651 | 0 | 2.689 | 0.37939 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | Electricity usage data was missing and has been calculated based on metered data | there are no meters for this building , except parking , do we want that ? |  | TRUE | TRUE | TRUE |  | E,G |  |  | 2.025
2023-02-01 | 2 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.835
2023-03-01 | 3 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.7325
2023-04-01 | 4 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.5396
2023-05-01 | 5 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.3846
2023-06-01 | 6 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.4127
2023-07-01 | 7 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.5036
2023-08-01 | 8 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.71
2023-09-01 | 9 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.8359
2023-10-01 | 10 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.8899
2023-11-01 | 11 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.864
2023-12-01 | 12 | Concession Buildings | South campus | 4320 | Storage | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.8979
2023-01-01 | 1 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 583.2634 |  |  |  | 0 | 1.3881 | 0 | 0 |  | 6.6345 |  |  |  | 6.6345 | CorpYard A: Gas (PG&E: 4755418303-9 / 4755418005) Usage |  | Summed areas -Corp Yard -Office and Trades | TRUE | TRUE | TRUE | Y | E |  |  |  | 1.945
2023-02-01 | 2 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 698.0412 |  |  |  | 0 | 1.6613 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 2.5298
2023-03-01 | 3 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 570.2473 |  |  |  | 0 | 1.3571 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 1.5202
2023-04-01 | 4 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 145.896 |  |  |  | 0 | 0.34721 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.3442
2023-05-01 | 5 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 19.3187 |  |  |  | 0 | 0.045976 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.070243
2023-06-01 | 6 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 0.4 |  |  |  | 0 | 0.00095195 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.039501
2023-07-01 | 7 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.039615
2023-08-01 | 8 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.039914
2023-09-01 | 9 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 0.8 |  |  |  | 0 | 0.0019039 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.041561
2023-10-01 | 10 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 42.0792 |  |  |  | 0 | 0.10014 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.13358
2023-11-01 | 11 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 174.2498 |  |  |  | 0 | 0.41469 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 0.4914
2023-12-01 | 12 | Corporation Yard Offices+Yard Trades | Main campus | 42019 | Office |  |  | 553.471 |  |  |  | 0 | 1.3172 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y |  |  |  |  | 1.5615
2018-01-01 | 1 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 163.2 | 0 | 0 | 0 | 0 |  |  |  |  | 5.3822 | 5.3822 | Suburban Propane: Corp Yard (1644-002486) Usage |  | propane is not used for bldg energy so not being used further | TRUE | TRUE | TRUE | Y | [24 empty] | 1.2765
2018-02-01 | 2 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 175.6 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.5199
2018-03-01 | 3 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 143.1 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.1302
2018-04-01 | 4 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 198.02 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.6075
2018-05-01 | 5 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 0 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 0
2018-06-01 | 6 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 205.6 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.6683
2018-07-01 | 7 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 114.6 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 0.90859
2018-08-01 | 8 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2018-09-01 | 9 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 383.8 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 3.1415
2018-10-01 | 10 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 160.1 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.351
2018-11-01 | 11 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2018-12-01 | 12 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | [5 empty] | 163.2 | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y | [24 empty] | 1.4097
2023-01-01 | 1 | Dining Commons | Main campus | 23925 | Food Service | 52353.3772 |  | 3716.8011 |  |  |  | 7.4662 | 15.5352 | 0 | 0 | 129.8267 | 155.3999 |  |  |  | 285.2267 | DC: Electric (PG&E: 0345535747-9 / 0345602583) Usage |  |  | FALSE | TRUE | TRUE | N |  |  |  | 10.7808 | 12.8868
2023-02-01 | 2 | Dining Commons | Main campus | 23925 | Food Service | 74900.1641 |  | 4573.1323 |  |  |  | 10.6817 | 19.1145 | 0 | 0 | [6 empty] | DC: Gas (PG&E: 0078358215-8 / 0078358005) Usage |  |  | FALSE | TRUE | TRUE | N |  |  |  | 14.4021 | 16.5692
2023-03-01 | 3 | Dining Commons | Main campus | 23925 | Food Service | 74200.0946 |  | 4173.6986 |  |  |  | 10.5818 | 17.4449 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 14.1968 | 11.2939
2023-04-01 | 4 | Dining Commons | Main campus | 23925 | Food Service | 85507.7674 |  | 3671.7639 |  |  |  | 12.1945 | 15.347 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 16.4185 | 6.8696
2023-05-01 | 5 | Dining Commons | Main campus | 23925 | Food Service | 73908.45 |  | 2648.8375 |  |  |  | 10.5403 | 11.0714 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 14.8542 | 4.3538
2023-06-01 | 6 | Dining Commons | Main campus | 23925 | Food Service | 53123.7867 |  | 1568.8581 |  |  |  | 7.5761 | 6.5574 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 13.8259 | 2.7602
2023-07-01 | 7 | Dining Commons | Main campus | 23925 | Food Service | 58396.5333 |  | 1393.5806 |  |  |  | 8.3281 | 5.8248 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 14.9882 | 2.499
2023-08-01 | 8 | Dining Commons | Main campus | 23925 | Food Service | 92134.28 |  | 2327.1613 |  |  |  | 13.1395 | 9.7269 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 20.0389 | 4.1611
2023-09-01 | 9 | Dining Commons | Main campus | 23925 | Food Service | 106109.7467 |  | 3204 |  |  |  | 15.1326 | 13.3918 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 22.5198 | 6.5346
2023-10-01 | 10 | Dining Commons | Main campus | 23925 | Food Service | 103674.3207 |  | 3512.3154 |  |  |  | 14.7852 | 14.6805 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 19.8854 | 7.751
2023-11-01 | 11 | Dining Commons | Main campus | 23925 | Food Service | 83654.3559 |  | 3536.2652 |  |  |  | 11.9301 | 14.7806 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 16.6131 | 9.1038
2023-12-01 | 12 | Dining Commons | Main campus | 23925 | Food Service | 52384.2834 |  | 2853.0194 |  |  |  | 7.4706 | 11.9248 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 11.9497 | 7.7919
2023-01-01 | 1 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 352147.5657 |  |  | 12726.4661 | 62484.2034 |  | 2.4068 | 0 | 2.5493 | 1.502 | 27.0034 | 0 | 13.668 | 29.274 |  | 69.9453 | MLK: Main Total Electric Usage © multipllied by 1000 minus tenants |  |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 336974.6406 |  |  | 12056.37 | 59577.1596 |  | 2.3031 | 0 | 2.415 | 1.4321 | [6 empty] | MLK: Steam Meter (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 356579.6211 |  |  | 10945.2542 | 67979.0583 |  | 2.4371 | 0 | 2.1925 | 1.634 | [6 empty] | MLK: CHW Meter (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 339422.1406 |  |  | 5662.6558 | 87620.5936 |  | 2.3198 | 0 | 1.1343 | 2.1062 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 345834.1406 |  |  | 4223.54 | 99531.7547 |  | 2.3637 | 0 | 0.84603 | 2.3925 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 324894.4015 |  |  | 2150.5244 | 114970.3959 |  | 2.2205 | 0 | 0.43078 | 2.7636 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 342248.5282 |  |  | 1287.0256 | 146697.8949 |  | 2.3391 | 0 | 0.25781 | 3.5262 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 325690.0893 |  |  | 894.3677 | 157307.5185 |  | 2.226 | 0 | 0.17915 | 3.7813 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 311702.0913 |  |  | 1484.6875 | 136612.1135 |  | 2.1304 | 0 | 0.2974 | 3.2838 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 315562.7491 |  |  | 2290.6848 | 124831.8004 |  | 2.1568 | 0 | 0.45885 | 3.0006 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 292523.337 |  |  | 5581.4674 | 83332.9225 |  | 1.9993 | 0 | 1.118 | 2.0031 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Dr. Martin Luther King, Jr. Library | Main campus | 499221 | Library | 307377.6107 |  |  | 8930.2416 | 76902.4175 |  | 2.1008 | 0 | 1.7888 | 1.8485 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 2781.0455 | [5 empty] | 3.8604 | 0 | 0 | 0 | [6 empty] | MLK: Bookstore Electric (M) Usage |  |  | FALSE | TRUE | TRUE | Y
2023-02-01 | 2 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1933.75 | [5 empty] | 2.6843 | 0 | 0 | 0 | [6 empty] | MLK: Market Cafe Electric (M) Usage |  |  | FALSE | TRUE | TRUE | Y
2023-03-01 | 3 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1837.8918 | [5 empty] | 2.5512 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-04-01 | 4 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1796.8582 | [5 empty] | 2.4943 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-05-01 | 5 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1852.25 | [5 empty] | 2.5711 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-06-01 | 6 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1293.2866 | [5 empty] | 1.7952 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-07-01 | 7 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1344.5884 | [5 empty] | 1.8665 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-08-01 | 8 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1198.4821 | [5 empty] | 1.6636 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-09-01 | 9 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1659.1521 | [5 empty] | 2.3031 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-10-01 | 10 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 1868.2407 | [5 empty] | 2.5933 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-11-01 | 11 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 2136.0648 | [5 empty] | 2.9651 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-12-01 | 12 | Dr. Martin Luther King, Jr. Library-Tenants | Main Campus | 2458 | Library | 2065.5344 | [5 empty] | 2.8672 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y
2023-01-01 | 1 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 34186.75 |  |  | 2894.34 | 0 |  | 1.5044 | 0 | 3.7329 | 0 | 15.0639 | 0 | 21.981 | 4.113 |  |  | Will's Manual Data- Electricity,steam |  | Summed areas - DMH and IRC | FALSE | FALSE | FALSE | Y |  | Y
2023-02-01 | 2 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 23741.75 |  |  | 1527.37 | 352.3599 |  | 1.0448 | 0 | 1.9699 | 0.054534 | [6 empty] | 2018-DMH: Chilled Water (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 23741.75 |  |  | 1527.37 | 45.8243 |  | 1.0448 | 0 | 1.9699 | 0.0070921 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 23741.75 |  |  | 1850.71 | 803.164 |  | 1.0448 | 0 | 2.3869 | 0.1243 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic |  |  |  |  | 1291.6487 |  | 0 | 0 | 0 | 0.1999 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 19481.75 |  |  | 41.71 | 1776.2885 |  | 0.8573 | 0 | 0.053794 | 0.27491 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 38486 |  |  | 63.26 | 4120.9546 |  | 1.6936 | 0 | 0.081588 | 0.63779 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 31514.25 |  |  | 323.58 | 9675.447 |  | 1.3868 | 0 | 0.41733 | 1.4974 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 35742 |  |  | 689.15 | 3793.8857 |  | 1.5728 | 0 | 0.88881 | 0.58717 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 39066.75 |  |  | 2555.79 | 4008.5521 |  | 1.7191 | 0 | 3.2963 | 0.62039 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 37266.25 |  |  | 2913.73 | 707.3798 |  | 1.6399 | 0 | 3.7579 | 0.10948 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Dudley Moorehead Hall + IRC | Main Campus | 77536 | Academic | 35349.5 |  |  | 2656.14 | 0 |  | 1.5556 | 0 | 3.4257 | 0 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Duncan Hall | Main campus | 345715 | Lab | 253251.3685 |  | 10.0016 | 30776.5517 | 33783.1314 |  | 2.4994 | 0.002893 | 8.9023 | 1.1726 | 29.8651 | 0.075595 | 69.7543 | 23.7307 |  | 123.4257 | Duncan Hall: Electricity 1 (M) Usage-- plus elec 2 minus verizon | Total elec minus verizon electric meter |  | FALSE | FALSE | FALSE | Y | [27 empty] | 1086606.9062 | 153413.4437
2023-02-01 | 2 | Duncan Hall | Main campus | 345715 | Lab | 252565.6866 |  | 31.0602 | 30750 | 30563.2305 |  | 2.4927 | 0.0089843 | 8.8946 | 1.0609 | [6 empty] | Duncan Hall: Electricity 2 (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [27 empty] | 1040767.0195 | 155000.6866
2023-03-01 | 3 | Duncan Hall | Main campus | 345715 | Lab | 271737.5886 |  | 16.4976 | 32716.4223 | 36002.6661 |  | 2.6819 | 0.004772 | 9.4634 | 1.2497 | [6 empty] | Duncan Hall: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [27 empty] | 1144308.2065 | 165319.5115
2023-04-01 | 4 | Duncan Hall | Main campus | 345715 | Lab | 265099.5757 |  | 14.2272 | 25953.8902 | 53678.6423 |  | 2.6164 | 0.0041153 | 7.5073 | 1.8632 | [6 empty] | Duncan Hall PG&E SMD: DH Gas (0203358207 / 0203358005) Usage |  |  | FALSE | FALSE | FALSE | Y | [27 empty] | 1095087.269 | 161680.1528
2023-05-01 | 5 | Duncan Hall | Main campus | 345715 | Lab | 249774.1068 |  | 9.8962 | 14236.25 | 41924.1042 |  | 2.4651 | 0.0028625 | 4.1179 | 1.4552 | [6 empty] | Duncan Hall: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [27 empty] | 962386.0303 | 163000.1068
2023-06-01 | 6 | Duncan Hall | Main campus | 345715 | Lab | 230638.9759 |  | 12.0505 | 11494.5536 | 58037.299 |  | 2.2763 | 0.0034857 | 3.3249 | 2.0145 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 825196.1135 | 154285.9759
2023-07-01 | 7 | Duncan Hall | Main campus | 345715 | Lab | 230248.28 |  | 3.3023 | 10124.5089 | 80692.1777 |  | 2.2724 | 0.0009552 | 2.9286 | 2.8009 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 855515.4961 | 151713.78
2023-08-01 | 8 | Duncan Hall | Main campus | 345715 | Lab | 223964.9089 |  | 24.3843 | 8876.5179 | 94908.3315 |  | 2.2104 | 0.0070533 | 2.5676 | 3.2943 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 796085.5703 | 144371.5232
2023-09-01 | 9 | Duncan Hall | Main campus | 345715 | Lab | 237845.9743 |  | 19.752 | 10843.8988 | 72012.7499 |  | 2.3474 | 0.0057134 | 3.1367 | 2.4996 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 1024787.7676 | 142850.5267
2023-10-01 | 10 | Duncan Hall | Main campus | 345715 | Lab | 261547.5364 |  | 25.1425 | 15682.7083 | 84458.186 |  | 2.5813 | 0.0072726 | 4.5363 | 2.9316 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 1193448.5957 | 147778.3698
2023-11-01 | 11 | Duncan Hall | Main campus | 345715 | Lab | 268530.4375 |  | 8.7418 | 25116.5192 | 56136.4616 |  | 2.6502 | 0.0025286 | 7.2651 | 1.9485 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 1162598.0156 | 159110.2773
2023-12-01 | 12 | Duncan Hall | Main campus | 345715 | Lab | 280824.0681 |  | 86.2886 | 24579.289 | 41474.3967 |  | 2.7716 | 0.024959 | 7.1097 | 1.4396 | [9 empty] | FALSE | FALSE | FALSE | Y | [27 empty] | 1192768.8789 | 168440.6765
2023-01-01 | 1 | Duncan Hall-Verizon | Main campus |  |  | 9208.4545 | [5 empty] | 0 | 0 | 0 | 0 | [6 empty] | DH: Verizon Electric (M) Usage |  |  | 0 | 0 | 0 | Y | [27 empty] | 1086606.9062 | 153413.4437
2023-02-01 | 2 | Duncan Hall-Verizon | Main campus |  |  | 8182 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1040767.0195 | 155000.6866
2023-03-01 | 3 | Duncan Hall-Verizon | Main campus |  |  | 9021.2035 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1144308.2065 | 165319.5115
2023-04-01 | 4 | Duncan Hall-Verizon | Main campus |  |  | 8908.7965 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1095087.269 | 161680.1528
2023-05-01 | 5 | Duncan Hall-Verizon | Main campus |  |  | 9138 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 962386.0303 | 163000.1068
2023-06-01 | 6 | Duncan Hall-Verizon | Main campus |  |  | 8852.5714 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 825196.1135 | 154285.9759
2023-07-01 | 7 | Duncan Hall-Verizon | Main campus |  |  | 9122.4286 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 855515.4961 | 151713.78
2023-08-01 | 8 | Duncan Hall-Verizon | Main campus |  |  | 9207.8857 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 796085.5703 | 144371.5232
2023-09-01 | 9 | Duncan Hall-Verizon | Main campus |  |  | 8977.5217 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1024787.7676 | 142850.5267
2023-10-01 | 10 | Duncan Hall-Verizon | Main campus |  |  | 9352.5926 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1193448.5957 | 147778.3698
2023-11-01 | 11 | Duncan Hall-Verizon | Main campus |  |  | 8772.9243 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1162598.0156 | 159110.2773
2023-12-01 | 12 | Duncan Hall-Verizon | Main campus |  |  | 8856.0757 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [27 empty] | 1192768.8789 | 168440.6765
2023-01-01 | 1 | Dwight Bentel Hall | Main campus | 36691 | Academic | 15064.6552 |  |  | 3065.9759 | 51.6456 |  | 1.4009 | 0 | 8.3562 | 0.016891 | 19.0632 | 0 | 40.781 | 3.9183 |  | 63.7625 | Dwight Bentel Hall: Electricity (M) Usage | chilled water data extracted from 2018 |  | FALSE | FALSE | FALSE | Y |  | Y
2023-02-01 | 2 | Dwight Bentel Hall | Main campus | 36691 | Academic | 16889 |  |  | 2823.8086 | 201.5897 |  | 1.5706 | 0 | 7.6962 | 0.065931 | [6 empty] | Dwight Bentel Hall: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Dwight Bentel Hall | Main campus | 36691 | Academic | 16249.72 |  |  | 2383.9213 | 114.4435 |  | 1.5111 | 0 | 6.4973 | 0.037429 | [6 empty] | 2018 - DBH: Chilled Water (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Dwight Bentel Hall | Main campus | 36691 | Academic | 17378.78 |  |  | 1413.0904 | 433.1981 |  | 1.6161 | 0 | 3.8513 | 0.14168 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Dwight Bentel Hall | Main campus | 36691 | Academic | 16967 |  |  | 851.0156 | 440.431 |  | 1.5778 | 0 | 2.3194 | 0.14405 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Dwight Bentel Hall | Main campus | 36691 | Academic | 16645.2857 |  |  | 421.9587 | 650.9382 |  | 1.5479 | 0 | 1.15 | 0.21289 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Dwight Bentel Hall | Main campus | 36691 | Academic | 18801.5291 |  |  | 161.7891 | 1637.0735 |  | 1.7484 | 0 | 0.44095 | 0.53541 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Dwight Bentel Hall | Main campus | 36691 | Academic | 20676.7293 |  |  | 3.5178 | 4210.1351 |  | 1.9228 | 0 | 0.0095876 | 1.3769 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Dwight Bentel Hall | Main campus | 36691 | Academic | 17616.28 |  |  | 0 | 2162.3318 |  | 1.6382 | 0 | 0 | 0.7072 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Dwight Bentel Hall | Main campus | 36691 | Academic | 18687.9259 |  |  | 174.1016 | 1760.8743 |  | 1.7378 | 0 | 0.47451 | 0.5759 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Dwight Bentel Hall | Main campus | 36691 | Academic | 18976.2563 |  |  | 2543.8222 | 266.0973 |  | 1.7647 | 0 | 6.9331 | 0.087029 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Dwight Bentel Hall | Main campus | 36691 | Academic | 11043.7523 |  |  | 1119.94 | 51.6456 |  | 1.027 | 0 | 3.0524 | 0.016891 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Engineering | Main campus | 341415 | Academic | 286377.338 |  |  | 14567.2306 | 19374.6964 |  | 2.862 | 0 | 4.2667 | 0.68098 | 36.3857 | 0 | 35.7775 | 36.9791 |  | 109.1422 | Eng Electric Meter (N4) Usage -divided by 10 |  |  | FALSE | FALSE | FALSE | Y | [29 empty] | 2863773.3799
2023-02-01 | 2 | Engineering | Main campus | 341415 | Academic | 278527.3741 |  |  | 14797.5 | 19665.88 |  | 2.7835 | 0 | 4.3342 | 0.69121 | [6 empty] | Engineering: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [29 empty] | 2785273.7412
2023-03-01 | 3 | Engineering | Main campus | 341415 | Academic | 312884.6304 |  |  | 16078.911 | 22997.6776 |  | 3.1269 | 0 | 4.7095 | 0.80832 | [6 empty] | Engineering: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [29 empty] | 3128846.3037
2023-04-01 | 4 | Engineering | Main campus | 341415 | Academic | 314388.7276 |  |  | 12523.589 | 71887.8498 |  | 3.1419 | 0 | 3.6681 | 2.5267 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3143887.2756
2023-05-01 | 5 | Engineering | Main campus | 341415 | Academic | 320838.9447 |  |  | 12476.5625 | 101593.5923 |  | 3.2064 | 0 | 3.6544 | 3.5708 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3208389.4467
2023-06-01 | 6 | Engineering | Main campus | 341415 | Academic | 275332.6112 |  |  | 3432.5076 | 109602.6089 |  | 2.7516 | 0 | 1.0054 | 3.8523 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 2753326.1118
2023-07-01 | 7 | Engineering | Main campus | 341415 | Academic | 302103.009 |  |  | 4968.2736 | 148445.0115 |  | 3.0191 | 0 | 1.4552 | 5.2175 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3021030.0898
2023-08-01 | 8 | Engineering | Main campus | 341415 | Academic | 285617.0762 |  |  | 3959.558 | 170042.268 |  | 2.8544 | 0 | 1.1597 | 5.9766 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 2856170.7622
2023-09-01 | 9 | Engineering | Main campus | 341415 | Academic | 323797.3443 |  |  | 4429.7186 | 130659.2451 |  | 3.2359 | 0 | 1.2975 | 4.5924 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3237973.4434
2023-10-01 | 10 | Engineering | Main campus | 341415 | Academic | 322579.452 |  |  | 5037.1296 | 117834.4791 |  | 3.2238 | 0 | 1.4754 | 4.1416 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3225794.5195
2023-11-01 | 11 | Engineering | Main campus | 341415 | Academic | 306935.4008 |  |  | 12502.0025 | 75735.6868 |  | 3.0674 | 0 | 3.6618 | 2.6619 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3069354.0078
2023-12-01 | 12 | Engineering | Main campus | 341415 | Academic | 311477.5785 |  |  | 17376.6775 | 64262.305 |  | 3.1128 | 0 | 5.0896 | 2.2587 | [9 empty] | FALSE | FALSE | FALSE | Y | [29 empty] | 3114775.7849
2023-01-01 | 1 | Field House | South campus | 15667 | Athletics | 8729.5697 |  | 582.371 |  |  |  | 1.9011 | 3.7172 | 0 | 0 | 27.0704 | 33.337 | 0 | 0 |  | 60.4073 | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Usage |  | Negative | FALSE | TRUE | TRUE |  |  |  | Solar to be added | 0.03434 | [26 empty] | 1.6 | 5483.2312 | 0.04 | 6716.34
2023-02-01 | 2 | Field House | South campus | 15667 | Athletics | 8433.9138 |  | 2035.0624 |  |  |  | 1.8368 | 12.9895 | 0 | 0 | [6 empty] | Field House: Gas (PG&E: 7088794250-9 / 7088794005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.034335 | [26 empty] | 1.6223 | 4382.2688 | 0.16 | 9734.32
2023-03-01 | 3 | Field House | South campus | 15667 | Athletics | 9424.7613 |  | 1363.9372 |  |  |  | 2.0525 | 8.7058 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034365 | [26 empty] | 1.7065 | 3852.7242 | 0.04 | 12793.1304
2023-04-01 | 4 | Field House | South campus | 15667 | Athletics | 8591.9995 |  | 355.0982 |  |  |  | 1.8712 | 2.2665 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034397 | [26 empty] | 1.3912 | 83.9424 | 0.28 | 11862.88
2023-05-01 | 5 | Field House | South campus | 15667 | Athletics | 8698.2223 |  | 156.4312 |  |  |  | 1.8943 | 0.99848 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.033564 | [26 empty] | 1.0288 | -4073.6 | 0.4 | 11256.24
2023-06-01 | 6 | Field House | South campus | 15667 | Athletics | 9406.7972 |  | 72.0516 |  |  |  | 2.0486 | 0.45989 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034269 | [26 empty] | 0.79204 | -5268.4909 | 0.92 | 9906.178
2023-07-01 | 7 | Field House | South campus | 15667 | Athletics | 9761.9302 |  | 60 |  |  |  | 2.126 | 0.38297 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034555 | [26 empty] | 1.188 | -3851.6677 | 0.92 | 11028.4856
2023-08-01 | 8 | Field House | South campus | 15667 | Athletics | 13076.2582 |  | 38.3484 |  |  |  | 2.8478 | 0.24477 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034577 | [26 empty] | 1.9323 | 5290.5586 | 0.96 | 10664.3348
2023-09-01 | 9 | Field House | South campus | 15667 | Athletics | 13072.9744 |  | 20.6 |  |  |  | 2.8471 | 0.13149 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | -0.00575 | [26 empty] | 2.0212 | 7645.95 | 0.56 | 10140.94
2023-10-01 | 10 | Field House | South campus | 15667 | Athletics | 12980.4851 |  | 64.8081 |  |  |  | 2.8269 | 0.41366 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.021408 | [26 empty] | 1.9269 | 7819.3031 | 0.36 | 10069.16
2023-11-01 | 11 | Field House | South campus | 15667 | Athletics | 11499.5505 |  | 257.1145 |  |  |  | 2.5044 | 1.6411 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.054575 | [26 empty] | 1.8594 | 7894.5276 | 0.16 | 9430
2023-12-01 | 12 | Field House | South campus | 15667 | Athletics | 10623.478 |  | 217.0774 |  |  |  | 2.3136 | 1.3856 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.12074 | [26 empty] | 1.9347 | 7996.6774 | 381.88 | 9956.64
2023-01-01 | 1 | Golf Complex |  |  |  | 8213.7863 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | Golf: Electric (PG&E: 4147571902-1 / 4148940516) Usage | not to be considered |  | TRUE | TRUE | TRUE |  |  |  | not to be considered | 1.9061 | [30 empty] | 5170.841
2023-02-01 | 2 | Golf Complex |  |  |  | 7195.4463 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.8705 | [30 empty] | 6856.52
2023-03-01 | 3 | Golf Complex |  |  |  | 7207.3436 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.784 | [30 empty] | 7202.198
2023-04-01 | 4 | Golf Complex |  |  |  | 5541.9067 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.4395 | [30 empty] | 5803.629
2023-05-01 | 5 | Golf Complex |  |  |  | 4869.7212 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.2406 | [30 empty] | 4551.758
2023-06-01 | 6 | Golf Complex |  |  |  | 4455.6501 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.2588 | [30 empty] | 4410.62
2023-07-01 | 7 | Golf Complex |  |  |  | 5139.3362 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.4953 | [30 empty] | 5259.876
2023-08-01 | 8 | Golf Complex |  |  |  | 5119.5484 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.5202 | [30 empty] | 5010.7744
2023-09-01 | 9 | Golf Complex |  |  |  | 5700.5024 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.7406 | [30 empty] | 5584.654
2023-10-01 | 10 | Golf Complex |  |  |  | 7119.9985 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 1.9911 | [30 empty] | 7268.841
2023-11-01 | 11 | Golf Complex |  |  |  | 8211.0746 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 2.3305 | [30 empty] | 8253.6269
2023-12-01 | 12 | Golf Complex |  |  |  | 8718.0531 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  |  | 2.5264 | [30 empty] | 8815.9839
2023-01-01 | 1 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 72853.9398 |  | 1539.5394 |  |  |  | 4.7034 | 2.913 | 0 | 0 | 68.1435 | 18.5483 | 0 | 0 |  | 86.6918 | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Usage |  |  | FALSE | TRUE | TRUE | [5 empty] | 5.0938 | [30 empty] | 0.020111 | 5.7448 | 27.0504 | 72853.9398 | 11.5818 | 72848.195 | 1198.0772 | 70363.05
2023-02-01 | 2 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 67513.4984 |  | 1948.6293 |  |  |  | 4.3586 | 3.687 | 0 | 0 | [6 empty] | HT: Gas (PG&E: 6290092604-9 / 6290092347) Usage |  |  | FALSE | TRUE | TRUE | [5 empty] | 7.102 | [30 empty] | -0.0017835 | 15.0982 | 26.5386 | 67513.4984 | 12.8247 | 67498.4002 | 2308.3687 | 70710.7501
2023-03-01 | 3 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 81000.5059 |  | 1661.9374 |  |  |  | 5.2293 | 3.1446 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 4.3299 | [30 empty] | 0.046728 | 50.9261 | 27.9519 | 81000.5059 | 14.6345 | 80949.5798 | 1604.7858 | 74742
2023-04-01 | 4 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 88848.6294 |  | 873.4655 |  |  |  | 5.736 | 1.6527 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 1.6687 | [30 empty] | 0.045148 | 42.244 | 32.6034 | 88848.6294 | 17.022 | 88806.3853 | 764.2496 | 94538.0999
2023-05-01 | 5 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 99004.4895 |  | 589.3893 |  |  |  | 6.3916 | 1.1152 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.97123 | [30 empty] | 0.047116 | 52.0692 | 36.9516 | 99004.4895 | 18.6863 | 98952.4203 | 623.1798 | 96440.7001
2023-06-01 | 6 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 87662.4313 |  | 543.4194 |  |  |  | 5.6594 | 1.0282 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.94552 | [30 empty] | 0.044152 | 38.7495 | 34.9773 | 87662.4313 | 18.0818 | 87623.6819 | 657.3468 | 90105.3
2023-07-01 | 7 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 96533.1253 |  | 100.7775 |  |  |  | 6.2321 | 0.19068 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.23492 | [30 empty] | 0.04329 | 31.2757 | 38.1967 | 96533.1253 | 20.5413 | 96501.8496 | 33.5496 | 98781.6
2023-08-01 | 8 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 99021.6074 |  | 35.7386 |  |  |  | 6.3927 | 0.067621 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.13327 | [30 empty] | 0.045985 | 39.6395 | 40.1329 | 99021.6074 | 21.664 | 98981.9679 | 26.3191 | 100605
2023-09-01 | 9 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 91521.5424 |  | 89.4597 |  |  |  | 5.9085 | 0.16927 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.25357 | [30 empty] | 0.030192 | 36.0474 | 35.5614 | 91521.5424 | 19.9384 | 91485.495 | 147.5581 | 90392.4
2023-10-01 | 10 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 97234.5274 |  | 253.8024 |  |  |  | 6.2773 | 0.48022 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 0.63973 | [30 empty] | 0.007075 | 35.5237 | 36.4428 | 97234.5274 | 19.3985 | 97199.0037 | 93.838 | 94773.9001
2023-11-01 | 11 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 88614.2794 |  | 740.7143 |  |  |  | 5.7208 | 1.4015 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 2.0006 | [30 empty] | 0.042656 | 29.6281 | 32.6645 | 88614.2794 | 18.1992 | 88584.6513 | 830.4007 | 89486.4001
2023-12-01 | 12 | Hammer Theater | Off Campus 3rd Street | 52851 | Theater | 85716.2473 |  | 1426.097 |  |  |  | 5.5337 | 2.6983 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | [5 empty] | 3.9557 | [30 empty] | 0.040425 | 21.3273 | 33.9472 | 85716.2473 | 17.1885 | 85694.92 | 1221.4326 | 82120.2
2023-01-01 | 1 | Health Building | Main campus | 42445 | Academic | 28607.203 |  |  | 2920.491 | 3871.7984 |  | 2.2996 | 0 | 6.8806 | 1.0946 | 28.4308 | 0 | 36.5378 | 34.7958 |  | 99.7644 | Health: Electricity (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Health Building | Main campus | 42445 | Academic | 27489.9902 |  |  | 2547.24 | 3255.1141 |  | 2.2098 | 0 | 6.0013 | 0.92028 | [6 empty] | Health: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Health Building | Main campus | 42445 | Academic | 29663.657 |  |  | 2671.6721 | 5646.1297 |  | 2.3846 | 0 | 6.2944 | 1.5963 | [6 empty] | Health: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Health Building | Main campus | 42445 | Academic | 28106.3625 |  |  | 1990.1529 | 11236.9894 |  | 2.2594 | 0 | 4.6888 | 3.1769 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Health Building | Main campus | 42445 | Academic | 30470.0317 |  |  | 1572.885 | 14028.7612 |  | 2.4494 | 0 | 3.7057 | 3.9662 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Health Building | Main campus | 42445 | Academic | 29117.1177 |  |  | 976.0071 | 16709.7598 |  | 2.3406 | 0 | 2.2995 | 4.7242 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Health Building | Main campus | 42445 | Academic | 29932.87 |  |  | 709.4704 | 19793.3206 |  | 2.4062 | 0 | 1.6715 | 5.5959 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Health Building | Main campus | 42445 | Academic | 26739.7164 |  |  | 166.5386 | 13280.898 |  | 2.1495 | 0 | 0.39236 | 3.7548 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Health Building | Main campus | 42445 | Academic | 30128.125 |  |  | 73.6142 | 11969.8295 |  | 2.4219 | 0 | 0.17343 | 3.3841 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Health Building | Main campus | 42445 | Academic | 32052.1415 |  |  | 219.0846 | 12346.0403 |  | 2.5766 | 0 | 0.51616 | 3.4905 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Health Building | Main campus | 42445 | Academic | 29549.1803 |  |  | 680.4494 | 7059.5807 |  | 2.3754 | 0 | 1.6031 | 1.9959 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Health Building | Main campus | 42445 | Academic | 31819.8088 |  |  | 980.8809 | 3877.3646 |  | 2.5579 | 0 | 2.3109 | 1.0962 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Hugh Gillis Hall | Main campus | 73315 | Academic | 41521.3528 |  |  |  | 4237.2872 |  | 1.9324 | 0 | 0 | 0.69355 | 27.0313 | 0 | 0 | 16.2501 |  | 43.2814 | Hugh Gillis Hall : Electricity (main) (M) Usage |  | Steam has bad data, consdered as missing and is being calculated for | FALSE | TRUE | FALSE | Y
2023-02-01 | 2 | Hugh Gillis Hall | Main campus | 73315 | Academic | 41570.0073 |  |  |  | 5228.9076 |  | 1.9346 | 0 | 0 | 0.85585 | [6 empty] | Hugh Gillis Hall : Electricity (mezzanine) (M) Usage |  |  | FALSE | TRUE | FALSE | Y
2023-03-01 | 3 | Hugh Gillis Hall | Main campus | 73315 | Academic | 47980.2874 |  |  |  | 7140.064 |  | 2.233 | 0 | 0 | 1.1687 | [6 empty] | Steam usage data was incomplete and has been calculated based on metered data | bad data |  | FALSE | TRUE | FALSE | Y
2023-04-01 | 4 | Hugh Gillis Hall | Main campus | 73315 | Academic | 45639.7077 |  |  |  | 7214.2753 |  | 2.124 | 0 | 0 | 1.1808 | [6 empty] | Hugh Gillis Hall : Chilled Water (M) Usage |  |  | FALSE | TRUE | FALSE | Y
2023-05-01 | 5 | Hugh Gillis Hall | Main campus | 73315 | Academic | 44350.0366 |  |  |  | 7305.41 |  | 2.064 | 0 | 0 | 1.1957 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-06-01 | 6 | Hugh Gillis Hall | Main campus | 73315 | Academic | 42468.2319 |  |  |  | 9466.6234 |  | 1.9764 | 0 | 0 | 1.5495 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-07-01 | 7 | Hugh Gillis Hall | Main campus | 73315 | Academic | 44341.7656 |  |  |  | 11782.3111 |  | 2.0636 | 0 | 0 | 1.9285 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-08-01 | 8 | Hugh Gillis Hall | Main campus | 73315 | Academic | 48935.6873 |  |  |  | 13633.4557 |  | 2.2774 | 0 | 0 | 2.2315 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-09-01 | 9 | Hugh Gillis Hall | Main campus | 73315 | Academic | 54626.1176 |  |  |  | 10639.7979 |  | 2.5422 | 0 | 0 | 1.7415 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-10-01 | 10 | Hugh Gillis Hall | Main campus | 73315 | Academic | 59338.0975 |  |  |  | 9489.2151 |  | 2.7615 | 0 | 0 | 1.5532 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-11-01 | 11 | Hugh Gillis Hall | Main campus | 73315 | Academic | 53488.6057 |  |  |  | 6660.0879 |  | 2.4893 | 0 | 0 | 1.0901 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-12-01 | 12 | Hugh Gillis Hall | Main campus | 73315 | Academic | 56571.8433 |  |  |  | 6484.0008 |  | 2.6328 | 0 | 0 | 1.0613 | [9 empty] | FALSE | TRUE | FALSE | Y
2023-01-01 | 1 | Industrial Studies | Main campus | 113302 | Lab | 28101.7225 |  | 764.4623 | 230.1478 |  |  | 0.84626 | 0.67471 | 0.20313 | 0 | 11.9823 | 12.4819 | 2.6921 | 0 |  | 27.1563 | Industrial Studies: Electricity (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-02-01 | 2 | Industrial Studies | Main campus | 113302 | Lab | 33390.0146 |  | 1681.5711 | 937.91 |  |  | 1.0055 | 1.4841 | 0.8278 | 0 | [6 empty] | Industrial Studies: Steam (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-03-01 | 3 | Industrial Studies | Main campus | 113302 | Lab | 33956.2867 |  | 1994.67 | 1180.2857 |  |  | 1.0226 | 1.7605 | 1.0417 | 0 | [6 empty] | Industrial Studies PG&E SMD: IS Gas (0328358199 / 0328358005) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-04-01 | 4 | Industrial Studies | Main campus | 113302 | Lab | 36440.6039 |  | 1807.9889 | 269.4801 |  |  | 1.0974 | 1.5957 | 0.23784 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-05-01 | 5 | Industrial Studies | Main campus | 113302 | Lab | 34013.0826 |  | 1229.1097 | 55.4717 |  |  | 1.0243 | 1.0848 | 0.048959 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-06-01 | 6 | Industrial Studies | Main campus | 113302 | Lab | 23341.4366 |  | 244.4169 | 57.3645 |  |  | 0.70291 | 0.21572 | 0.05063 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-07-01 | 7 | Industrial Studies | Main campus | 113302 | Lab | 28939.5024 |  | 230.6865 | 38.5801 |  |  | 0.87149 | 0.2036 | 0.034051 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-08-01 | 8 | Industrial Studies | Main campus | 113302 | Lab | 34460.2468 |  | 929.1771 | 0.87953 |  |  | 1.0377 | 0.82009 | 0.00077627 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-09-01 | 9 | Industrial Studies | Main campus | 113302 | Lab | 36044.0586 |  | 1212.4436 | 7.2731 |  |  | 1.0854 | 1.0701 | 0.0064192 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-10-01 | 10 | Industrial Studies | Main campus | 113302 | Lab | 39814.7922 |  | 1574.9001 | 13.5241 |  |  | 1.199 | 1.39 | 0.011936 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-11-01 | 11 | Industrial Studies | Main campus | 113302 | Lab | 37459.2242 |  | 1598.2894 | 120.1163 |  |  | 1.1281 | 1.4106 | 0.10601 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-12-01 | 12 | Industrial Studies | Main campus | 113302 | Lab | 31933.9011 |  | 874.5679 | 139.1252 |  |  | 0.96166 | 0.77189 | 0.12279 | 0 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-01-01 | 1 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 55682.3185 |  |  | 5226.1601 | 15687.9529 |  | 1.1622 | 0 | 3.1969 | 1.1516 | 45.1251 | 0 | 51.7528 | 61.5934 |  | 158.4714 | ISB Temp Electric 2 (M) Usage | miising months |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 58473.3276 |  |  | 5226.1601 | 15687.9529 |  | 1.2204 | 0 | 3.1969 | 1.1516 | [6 empty] | ISB: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 183932.6683 |  |  | 5226.1601 | 15687.9529 |  | 3.839 | 0 | 3.1969 | 1.1516 | [6 empty] | ISB: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 192719.1764 |  |  | 4292.6021 | 22277.1755 |  | 4.0224 | 0 | 2.6258 | 1.6353 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 199647.7203 |  |  | 8595.9559 | 67825.8537 |  | 4.167 | 0 | 5.2582 | 4.9788 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 191985.8355 |  |  | 10371.7502 | 104291.5055 |  | 4.007 | 0 | 6.3445 | 7.6555 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 198248.6108 |  |  | 9616.2627 | 153533.2748 |  | 4.1378 | 0 | 5.8824 | 11.2702 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 190209.9029 |  |  | 8927.2128 | 195080.3537 |  | 3.97 | 0 | 5.4609 | 14.3199 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 204257.9859 |  |  | 9264.0638 | 131362.2632 |  | 4.2632 | 0 | 5.6669 | 9.6427 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 230914.8175 |  |  | 6662.6026 | 86088.2685 |  | 4.8196 | 0 | 4.0756 | 6.3193 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 234665.8189 |  |  | 5034.8303 | 22466.1165 |  | 4.8978 | 0 | 3.0799 | 1.6491 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Interdisciplinary Science Building | Main campus | 163476 | Lab | 221300.7013 |  |  | 6159.718 | 9098.7303 |  | 4.6189 | 0 | 3.768 | 0.66789 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | International House | Off Campus 11th St | 25320 | Residential | 8470.6003 |  | 948.5484 |  |  |  | 1.1415 | 3.7462 | 0 | 0 | 15.0903 | 33.4447 | 0 | 0 |  | 48.535 | Foundation: Int'l House Electric (PG&E: 6630417140-9 / 6630417801) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 3.1673 | 3.3007
2023-02-01 | 2 | International House | Off Campus 11th St | 25320 | Residential | 8602.3079 |  | 1038.8849 |  |  |  | 1.1592 | 4.103 | 0 | 0 | [6 empty] | Foundation: Int'l House Gas (PG&E: 6672083804-5 / 6672083005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 3.3925 | 3.906
2023-03-01 | 3 | International House | Off Campus 11th St | 25320 | Residential | 9671.672 |  | 964.358 |  |  |  | 1.3033 | 3.8087 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.4533 | 2.655
2023-04-01 | 4 | International House | Off Campus 11th St | 25320 | Residential | 9632.5278 |  | 753.8024 |  |  |  | 1.298 | 2.9771 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.4222 | 1.4479
2023-05-01 | 5 | International House | Off Campus 11th St | 25320 | Residential | 9385.8527 |  | 620.0063 |  |  |  | 1.2648 | 2.4487 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.3839 | 1.0371
2023-06-01 | 6 | International House | Off Campus 11th St | 25320 | Residential | 8647.2547 |  | 471.6258 |  |  |  | 1.1653 | 1.8627 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 4.4385 | 0.84477
2023-07-01 | 7 | International House | Off Campus 11th St | 25320 | Residential | 9297.2929 |  | 400.5161 |  |  |  | 1.2529 | 1.5818 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 4.9724 | 0.73207
2023-08-01 | 8 | International House | Off Campus 11th St | 25320 | Residential | 10461.9071 |  | 408.6581 |  |  |  | 1.4098 | 1.614 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 5.3491 | 0.7549
2023-09-01 | 9 | International House | Off Campus 11th St | 25320 | Residential | 10509.3267 |  | 567 |  |  |  | 1.4162 | 2.2393 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 5.3196 | 1.1825
2023-10-01 | 10 | International House | Off Campus 11th St | 25320 | Residential | 10329.2801 |  | 662.8081 |  |  |  | 1.3919 | 2.6177 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.9441 | 1.4871
2023-11-01 | 11 | International House | Off Campus 11th St | 25320 | Residential | 9081.9204 |  | 791.9532 |  |  |  | 1.2238 | 3.1278 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.4568 | 2.0657
2023-12-01 | 12 | International House | Off Campus 11th St | 25320 | Residential | 7892.8508 |  | 840.0387 |  |  |  | 1.0636 | 3.3177 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.1551 | 2.3203
2019-01-01 | 1 | Joe West Hall | Main campus | 130000 | Residential | 49745.4 |  | 4265.6995 |  |  |  | 1.3056 | 3.2813 | 0 | 0 | [6 empty] | Joe West Hall PG&E SMD: JW Electric (8262196692 / 8264358394) Usage |  |  | FALSE | TRUE | TRUE | N
2019-02-01 | 2 | Joe West Hall | Main campus | 130000 | Residential | 67316.1 |  | 6382.6745 |  |  |  | 1.7668 | 4.9097 | 0 | 0 | [6 empty] | Joe West Hall PG&E SMD: JW Gas (4564269832 / 4560082337) Usage |  |  | FALSE | TRUE | TRUE | N
2019-03-01 | 3 | Joe West Hall | Main campus | 130000 | Residential | 68645.1 |  | 5266.669 |  |  |  | 1.8017 | 4.0513 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-04-01 | 4 | Joe West Hall | Main campus | 130000 | Residential | 63880.5 |  | 3307.6366 |  |  |  | 1.6766 | 2.5443 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-05-01 | 5 | Joe West Hall | Main campus | 130000 | Residential | 59289.6 |  | 2967.1136 |  |  |  | 1.5561 | 2.2824 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-06-01 | 6 | Joe West Hall | Main campus | 130000 | Residential | 39449.25 |  | 1402.441 |  |  |  | 1.0354 | 1.0788 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-07-01 | 7 | Joe West Hall | Main campus | 130000 | Residential | 42106.5 |  | 1506.7151 |  |  |  | 1.1051 | 1.159 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-08-01 | 8 | Joe West Hall | Main campus | 130000 | Residential | 59153.7 |  | 1522.9008 |  |  |  | 1.5526 | 1.1715 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-09-01 | 9 | Joe West Hall | Main campus | 130000 | Residential | 74686.7999 |  | 2198.0416 |  |  |  | 1.9602 | 1.6908 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-10-01 | 10 | Joe West Hall | Main campus | 130000 | Residential | 70525.35 |  | 3221.4297 |  |  |  | 1.851 | 2.478 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-11-01 | 11 | Joe West Hall | Main campus | 130000 | Residential | 63027.75 |  | 4157.9169 |  |  |  | 1.6542 | 3.1984 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2019-12-01 | 12 | Joe West Hall | Main campus | 130000 | Residential | 54628.95 |  | 4941.0768 |  |  |  | 1.4338 | 3.8008 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N
2023-01-01 | 1 | Koret Center | South campus | 15358 | Athletics | 36004.6701 |  | 1599.9161 |  |  |  | 7.999 | 10.4175 | 0 | 0 | 47.2726 | 43.3358 | 0 | 0 |  | 90.6084 | Koret Ctr: Electric (PG&E: 4147571902-1 / 4141854321) Usage |  | Negative | FALSE | TRUE | TRUE |  |  |  | solar to be added
2023-02-01 | 2 | Koret Center | South campus | 15358 | Athletics | 17368.14 |  | 1722.8 |  |  |  | 3.8586 | 11.2176 | 0 | 0 | [6 empty] | Koret Ctr: Gas (PG&E: 4147571902-1 / 9620442005) Usage |  |  | FALSE | TRUE | TRUE
2023-03-01 | 3 | Koret Center | South campus | 15358 | Athletics | 13117.3754 |  | 1344.4173 |  |  |  | 2.9142 | 8.7539 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-04-01 | 4 | Koret Center | South campus | 15358 | Athletics | 15397.6712 |  | 690.8827 |  |  |  | 3.4208 | 4.4985 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-05-01 | 5 | Koret Center | South campus | 15358 | Athletics | 15741.8276 |  | 296.2667 |  |  |  | 3.4973 | 1.9291 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-06-01 | 6 | Koret Center | South campus | 15358 | Athletics | 17024.1889 |  | 104.2636 |  |  |  | 3.7822 | 0.67889 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-07-01 | 7 | Koret Center | South campus | 15358 | Athletics | 17666.8999 |  | 71.1421 |  |  |  | 3.925 | 0.46323 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-08-01 | 8 | Koret Center | South campus | 15358 | Athletics | 21088.3665 |  | 67.4276 |  |  |  | 4.6851 | 0.43904 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-09-01 | 9 | Koret Center | South campus | 15358 | Athletics | 18999.6946 |  | 151.9625 |  |  |  | 4.2211 | 0.98947 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-10-01 | 10 | Koret Center | South campus | 15358 | Athletics | 17594.7818 |  | 295.8478 |  |  |  | 3.9089 | 1.9263 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-11-01 | 11 | Koret Center | South campus | 15358 | Athletics | 12940.6919 |  | 165.1381 |  |  |  | 2.875 | 1.0753 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-12-01 | 12 | Koret Center | South campus | 15358 | Athletics | 9837.9187 |  | 145.4516 |  |  |  | 2.1856 | 0.94707 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE
2023-01-01 | 1 | MacQuarrie Hall | Main campus | 107302 | Academic | 75903.4981 |  |  | 2243.7705 | 24.298 |  | 2.4136 | 0 | 2.0911 | 0.0027173 | 30.9637 | 0 | 17.9083 | 8.4125 |  | 57.2845 | MacQuarrie Hall: Electricity (M) Usage (minus 2022 Spartan) |  | The MQH: Elec Spartan Shops (M) is a submeter in MacQuarrie Hall for the food service tenant. It has been subtracted and area is not subtracted as they also use steam/CHW | FALSE | FALSE | FALSE | Y | [46 empty] | 2243.7705 |  | 156.1456 | 0.24219 | 5534.803 | 23199.0881 |  | -5534.803 | 980778.3398
2023-02-01 | 2 | MacQuarrie Hall | Main campus | 107302 | Academic | 69008.1875 |  |  | 2246.1426 | 43.5367 |  | 2.1943 | 0 | 2.0933 | 0.0048689 | [6 empty] | MacQuarrie Hall: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [46 empty] | 2246.1426 |  | 148.7849 | 0.52051 | 2129.125 | 25904.8125 |  | -2129.125 | 934117.6362
2023-03-01 | 3 | MacQuarrie Hall | Main campus | 107302 | Academic | 74379.6659 |  |  | 3244.6809 | 1326.2893 |  | 2.3651 | 0 | 3.0239 | 0.14832 | [6 empty] | MacQuarrie Hall: Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [46 empty] | 3244.6809 |  | 360.3937 | 15.665 | 2303.9106 | 27293.9195 |  | -2303.9106 | 1000308.5709
2023-04-01 | 4 | MacQuarrie Hall | Main campus | 107302 | Academic | 68192.6466 |  |  | 2151.364 | 5109.3257 |  | 2.1684 | 0 | 2.005 | 0.5714 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 2151.364 |  | 1094.9972 | 48.8994 | 1249.9644 | 29053.768 |  | -1249.9644 | 951498.6641
2023-05-01 | 5 | MacQuarrie Hall | Main campus | 107302 | Academic | 68133.5 |  |  | 1720.498 | 5744.8874 |  | 2.1665 | 0 | 1.6034 | 0.64247 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 1720.498 |  | 1259.5058 | 65.8486 | 0.625 | 26800.5 |  | -0.625 | 951998.7764
2023-06-01 | 6 | MacQuarrie Hall | Main campus | 107302 | Academic | 65876.5179 |  |  | 790.8231 | 8364.0627 |  | 2.0947 | 0 | 0.73701 | 0.93539 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 790.8231 |  | 1240.575 | 92.4922 | 0 | 19164.9107 |  | 0 | 817897.0889
2023-07-01 | 7 | MacQuarrie Hall | Main campus | 107302 | Academic | 71457.2321 |  |  | 465.0656 | 11513.8042 |  | 2.2722 | 0 | 0.43342 | 1.2876 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 465.0656 |  | 1669.6781 | 126.9531 | 0 | 20535.3393 |  | 0 | 896158.0508
2023-08-01 | 8 | MacQuarrie Hall | Main campus | 107302 | Academic | 101125.6828 |  |  | 339.7199 | 15554.0862 |  | 3.2156 | 0 | 0.3166 | 1.7395 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 339.7199 |  | 2682.5587 | 185.4756 | 0 | 172.5743 |  | 0 | 929779.0312
2023-09-01 | 9 | MacQuarrie Hall | Main campus | 107302 | Academic | 98261.2698 |  |  | 719.7786 | 12823.7081 |  | 3.1245 | 0 | 0.6708 | 1.4341 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 719.7786 |  | 2638.1969 | 140.2275 | 0 | 232.473 |  | 0 | 969288.2188
2023-10-01 | 10 | MacQuarrie Hall | Main campus | 107302 | Academic | 102981.0034 |  |  | 971.0386 | 10158.3432 |  | 3.2746 | 0 | 0.90496 | 1.136 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 971.0386 |  | 2489.3923 | 98.167 | 0 | 252.9966 |  | 0 | 996540.1562
2023-11-01 | 11 | MacQuarrie Hall | Main campus | 107302 | Academic | 93665.2573 |  |  | 1922.9076 | 3231.8863 |  | 2.9784 | 0 | 1.7921 | 0.36143 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 1922.9076 |  | 1092.9326 | 33.2314 | 0 | 233.8549 |  | 0 | 921938.4004
2023-12-01 | 12 | MacQuarrie Hall | Main campus | 107302 | Academic | 84774.8436 |  |  | 2400.1827 | 1328.7616 |  | 2.6957 | 0 | 2.2368 | 0.1486 | [9 empty] | FALSE | FALSE | FALSE | Y | [46 empty] | 2400.1827 |  | 556.0881 | 13.1973 | 0 | 194.32 |  | 0 | 848278.4751
2022-01-01 | 1 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 22164.1795 | [5 empty] | 20.3072 | 0 | 0 | 0 | [5 empty] | 0 | 2022 - MQH: Elec Spartan Shops (M) Usage |  |  | FALSE | TRUE | TRUE | Y | [46 empty] | 2243.7705 |  | 156.1456 | 0.24219 | 5534.803 | 23199.0881 |  | -5534.803 | 980778.3398
2022-02-01 | 2 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 23271.375 | [5 empty] | 21.3217 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 2246.1426 |  | 148.7849 | 0.52051 | 2129.125 | 25904.8125 |  | -2129.125 | 934117.6362
2022-03-01 | 3 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 27539.2344 | [5 empty] | 25.232 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 3244.6809 |  | 360.3937 | 15.665 | 2303.9106 | 27293.9195 |  | -2303.9106 | 1000308.5709
2022-04-01 | 4 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 26522.9335 | [5 empty] | 24.3008 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 2151.364 |  | 1094.9972 | 48.8994 | 1249.9644 | 29053.768 |  | -1249.9644 | 951498.6641
2022-05-01 | 5 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 24931.2853 | [5 empty] | 22.8425 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 1720.498 |  | 1259.5058 | 65.8486 | 0.625 | 26800.5 |  | -0.625 | 951998.7764
2022-06-01 | 6 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 21029.8125 | [5 empty] | 19.2679 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 790.8231 |  | 1240.575 | 92.4922 | 0 | 19164.9107 |  | 0 | 817897.0889
2022-07-01 | 7 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 21386.5488 | [5 empty] | 19.5948 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 465.0656 |  | 1669.6781 | 126.9531 | 0 | 20535.3393 |  | 0 | 896158.0508
2022-08-01 | 8 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 27973.9824 | [5 empty] | 25.6303 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 339.7199 |  | 2682.5587 | 185.4756 | 0 | 172.5743 |  | 0 | 929779.0312
2022-09-01 | 9 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 28670.25 | [5 empty] | 26.2682 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 719.7786 |  | 2638.1969 | 140.2275 | 0 | 232.473 |  | 0 | 969288.2188
2022-10-01 | 10 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 30877.0625 | [5 empty] | 28.2902 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 971.0386 |  | 2489.3923 | 98.167 | 0 | 252.9966 |  | 0 | 996540.1562
2022-11-01 | 11 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 26567.2813 | [5 empty] | 24.3415 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 1922.9076 |  | 1092.9326 | 33.2314 | 0 | 233.8549 |  | 0 | 921938.4004
2022-12-01 | 12 | MacQuarrie Hall- Spartan Shops | Main Campus | 3724 | Food Sale | 21534.2557 | [5 empty] | 19.7301 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y | [46 empty] | 2400.1827 |  | 556.0881 | 13.1973 | 0 | 194.32 |  | 0 | 848278.4751
2023-01-01 | 1 | Modular F,A,B | Main Campus | 6451 | Office | 6799.4327 | [5 empty] | 3.5963 | 0 | 0 | 0 | 39.7241 | 0 | 0 | 0 |  | 39.7241 | Mod F: Electric (PG&E: 4672084975-4 / 4672084566) Usage |  | Summed areas - Main campusMod A/B and F | FALSE | TRUE | TRUE | N |  |  |  | 2.8499
2023-02-01 | 2 | Modular F,A,B | Main Campus | 6451 | Office | 7317.3945 | [5 empty] | 3.8702 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 3.4299
2023-03-01 | 3 | Modular F,A,B | Main Campus | 6451 | Office | 7572.5787 | [5 empty] | 4.0052 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 3.29
2023-04-01 | 4 | Modular F,A,B | Main Campus | 6451 | Office | 6446.9297 | [5 empty] | 3.4098 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.9137
2023-05-01 | 5 | Modular F,A,B | Main Campus | 6451 | Office | 5945.5359 | [5 empty] | 3.1447 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.6505
2023-06-01 | 6 | Modular F,A,B | Main Campus | 6451 | Office | 5593.1733 | [5 empty] | 2.9583 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.8059
2023-07-01 | 7 | Modular F,A,B | Main Campus | 6451 | Office | 6015.1655 | [5 empty] | 3.1815 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 3.0645
2023-08-01 | 8 | Modular F,A,B | Main Campus | 6451 | Office | 6428.5878 | [5 empty] | 3.4001 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 3.2985
2023-09-01 | 9 | Modular F,A,B | Main Campus | 6451 | Office | 5866.7433 | [5 empty] | 3.103 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 3.0967
2023-10-01 | 10 | Modular F,A,B | Main Campus | 6451 | Office | 5715.5019 | [5 empty] | 3.023 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.7099
2023-11-01 | 11 | Modular F,A,B | Main Campus | 6451 | Office | 5548.9721 | [5 empty] | 2.9349 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.6683
2023-12-01 | 12 | Modular F,A,B | Main Campus | 6451 | Office | 5855.572 | [5 empty] | 3.0971 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  | 2.8189
2023-01-01 | 1 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 69646.4452 | 14562.7164 | 4720.1935 |  |  |  | 3.8917 | 7.7302 | 0 | 0 | 46.6938 | 64.0066 | 0 | 0 |  | 110.7004 | MLML: Main Electric (PG&E: 9928867424-7 / 9928500055) Usage | Pump house and boats electric/gas is not counted- Process loads? | Summed areas - Main Lab, aquaculture facility and marine operations | FALSE | TRUE | TRUE |  |  |  |  | 16.1934 | 14.1908 | [52 empty] | 6.3859 | 26050.67 | 0.043336 | 85.3824 | 3.7185 | 14477.334 | 1.1316 | 340.9677 | 0.41246 | 1087.1851 | 0.13324 | 37.6167 | 70026.87 |  |  | 48.835
2023-02-01 | 2 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 66994 | 13477.8038 | 4739.2763 |  |  |  | 3.7435 | 7.7614 | 0 | 0 | [6 empty] | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Usage | Main and sea lion gas is added |  | FALSE | TRUE | TRUE |  |  |  |  | 16.6521 | 15.2874 | [52 empty] | 5.8838 | 23967.3043 | -0.016667 | 40.3045 | 3.7819 | 13437.4994 | 1.2145 | 336.9323 | 0.45956 | 1114.7055 | 0.21698 | 59.0333 | 67420.96 |  |  | 18.365
2023-03-01 | 3 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 73143.6226 | 14108.2081 | 4919.2249 |  |  |  | 4.0871 | 8.0561 | 0 | 0 | [6 empty] | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 16.5001 | 11.841 | [52 empty] | 6.7313 | 28103.5972 | 0.0086027 | 15.6705 | 3.752 | 14092.5376 | 0.78289 | 293.7619 | 0.48194 | 1272.3987 | 0.14219 | 49.9715 | 72577.08 |  |  | 29.231
2023-04-01 | 4 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 69803.5774 | 12865.0101 | 4257.1147 |  |  |  | 3.9005 | 6.9718 | 0 | 0 | [6 empty] | MLML: Main Gas (PG&E: 4348987890-0 / 4348987005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 16.3289 | 7.0651 | [52 empty] | 6.1188 | 27020.7742 | 0.01769 | 12.0401 | 3.444 | 12852.9699 | 0.37907 | 198.8069 | 0.44577 | 1123.6643 | 0.057342 | 23.5285 | 70166.2 |  |  | 10.103
2023-05-01 | 5 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 69574.5806 | 12786.116 | 3241.2421 |  |  |  | 3.8877 | 5.3081 | 0 | 0 | [6 empty] | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 16.4788 | 4.8395 | [52 empty] | 6.7663 | 28123.5375 | 0.017141 | 10.7001 | 3.5061 | 12775.4158 | 0.20764 | 121.1313 | 0.45999 | 1186.5983 | 0.028142 | 10.9667 | 71262.54 |  |  | 11.92
2023-06-01 | 6 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 67851.9194 | 12016.5825 | 2128.1097 |  |  |  | 3.7914 | 3.4852 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 18.733 | 3.439 | [52 empty] | 7.7393 | 26212.3693 | 0.018734 | 13.491 | 3.8966 | 12003.0915 | 0.12148 | 61.9806 | 0.54697 | 1284.9333 | 0.01988 | 5.4667 | 68657.72 |  |  | 13.158
2023-07-01 | 7 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 69741.4655 | 12515.7807 | 1871.4116 |  |  |  | 3.897 | 3.0648 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 20.4975 | 3.0777 | [52 empty] | 7.1526 | 25623.6694 | 0.01662 | 8.6626 | 4.2338 | 12507.1181 | 0.10995 | 53.7987 | 0.51456 | 1187.3608 | 0.017261 | 3.7356 | 69408.6701 |  |  | 8.243
2023-08-01 | 8 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 70459.8345 | 12295.6111 | 1693.7804 |  |  |  | 3.9371 | 2.7739 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 20.9769 | 2.9683 | [52 empty] | 8.1725 | 26894.8351 | 0.025426 | 29.3874 | 4.2157 | 12266.2238 | 0.064338 | 24.8707 | 0.56323 | 1290.2458 | 0.016689 | 3.131 | 70122.9 |  |  | 34.942
2023-09-01 | 9 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 69127.7625 | 11529.3645 | 1199.9346 |  |  |  | 3.8627 | 1.9651 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 20.5979 | 2.4183 | [52 empty] | 7.949 | 25743.5278 | -0.021155 | 23.2078 | 4.0697 | 11506.1567 | 0.067494 | 23.1346 | 0.56676 | 1242.4933 | 0.018429 | 3.55 | 69547.87 |  |  | 18.68
2023-10-01 | 10 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 71846.3557 | 11818.2049 | 2005.4735 |  |  |  | 4.0146 | 3.2843 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 19.0666 | 4.4786 | [52 empty] | 6.9154 | 27226.4524 | 0.012576 | 19.1686 | 3.5639 | 11799.0364 | 0.035839 | 6.5809 | 0.53765 | 1233.6493 | 0.02188 | 4.8655 | 71916.52 |  |  | 18.644
2023-11-01 | 11 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 70198.4366 | 11917.7373 | 3940.0128 |  |  |  | 3.9225 | 6.4525 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 18.3031 | 9.7667 | [52 empty] | 7.627 | 27276.5233 | 0.016422 | 6.8683 | 3.6181 | 11910.869 | 0.28995 | 103.228 | 0.49435 | 1093.6912 | 0.03677 | 9.9006 | 69202.52 |  |  | 7.868
2023-12-01 | 12 | Moss Landing Marine Lab Main Laboratory | Moss Landing | 61062 | Lab | 67256.7097 | 12177.7649 | 4367.929 |  |  |  | 3.7581 | 7.1533 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 17.7598 | 11.3709 | [52 empty] | 7.6942 | 29715.2049 | 0.01716 | 8.267 | 3.7476 | 12169.498 | 0.51007 | 179.4065 | 0.49232 | 1084.0529 | 0.06943 | 21.2258 | 67347.73 |  |  | 5.559
2023-01-01 | 1 | Music | Main campus | 64072 | Academic | 23269.1034 |  |  | 6544.5801 | 9734.4266 |  | 1.2391 | 0 | 10.2144 | 1.8232 | 17.2441 | 0 | 80.7805 | 46.6622 |  | 144.6869 | Music: Electricity (M) Usage |  |  | FALSE | TRUE | FALSE | Y |  | Y | [72 empty] | 4068.2415 | 2476.3386 |  | 158580.8008
2023-02-01 | 2 | Music | Main campus | 64072 | Academic | 23881 |  |  | 5881.3574 | 11382.1234 |  | 1.2717 | 0 | 9.1793 | 2.1317 | [6 empty] | Music: Steam 1 (M) Usage |  |  | FALSE | TRUE | FALSE | Y | [74 empty] | 3676.4453 | 2204.9121 |  | 143310.3945
2023-03-01 | 3 | Music | Main campus | 64072 | Academic | 26970.201 |  |  | 6260.1005 | 13785.3821 |  | 1.4362 | 0 | 9.7704 | 2.5819 | [6 empty] | Music: Steam 2 (M) Usage |  |  | FALSE | TRUE | FALSE | Y | [74 empty] | 3822.6179 | 2437.4826 |  | 151671.8789
2023-04-01 | 4 | Music | Main campus | 64072 | Academic | 30375.799 |  |  | 5573.4152 | 19761.1286 |  | 1.6176 | 0 | 8.6987 | 3.701 | [6 empty] | 2018 - Music: Chilled Water (M) Usage - Archived |  |  | FALSE | TRUE | FALSE | Y | [74 empty] | 3040.9173 | 2532.4979 |  | 126524.6914
2023-05-01 | 5 | Music | Main campus | 64072 | Academic | 29585.5 |  |  | 3726.2012 | 22531.8356 |  | 1.5755 | 0 | 5.8156 | 4.22 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 2331.3477 | 1394.8535 |  | 132556.166
2023-06-01 | 6 | Music | Main campus | 64072 | Academic | 28948.1098 |  |  | 2906.5072 | 21646.8595 |  | 1.5416 | 0 | 4.5363 | 4.0542 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 1452.2104 | 1454.2969 |  | 116282.545
2023-07-01 | 7 | Music | Main campus | 64072 | Academic | 30926.8902 |  |  | 2558.1705 | 27252.4538 |  | 1.6469 | 0 | 3.9926 | 5.1041 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 1362.1646 | 1196.0059 |  | 118623.6367
2023-08-01 | 8 | Music | Main campus | 64072 | Academic | 29393.35 |  |  | 2110.6468 | 50984.5004 |  | 1.5653 | 0 | 3.2942 | 9.5489 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 1066.7667 | 1043.88 |  | 108481.3085
2023-09-01 | 9 | Music | Main campus | 64072 | Academic | 26233.0607 |  |  | 2042.7663 | 28118.7847 |  | 1.397 | 0 | 3.1882 | 5.2663 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 497.9947 | 1544.7716 |  | 130467.2803
2023-10-01 | 10 | Music | Main campus | 64072 | Academic | 26451.3393 |  |  | 2289.3604 | 26369.6463 |  | 1.4086 | 0 | 3.5731 | 4.9388 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 425.4534 | 1863.9069 |  | 139665.335
2023-11-01 | 11 | Music | Main campus | 64072 | Academic | 25691.7809 |  |  | 5600.28 | 10590.7308 |  | 1.3682 | 0 | 8.7406 | 1.9835 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 3260.372 | 2339.908 |  | 170937.2139
2023-12-01 | 12 | Music | Main campus | 64072 | Academic | 22091.8484 |  |  | 6264.3267 | 6987.3749 |  | 1.1764 | 0 | 9.777 | 1.3087 | [9 empty] | FALSE | TRUE | FALSE | Y | [74 empty] | 3732.7105 | 2531.6162 |  | 167020.4121
2023-01-01 | 1 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 12520.8724 | [5 empty] | 0.3455 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.6286
2023-02-01 | 2 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 13518.5811 | [5 empty] | 0.37303 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.6841
2023-03-01 | 3 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 15210.5671 | [5 empty] | 0.41972 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 4.3677
2023-04-01 | 4 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 15992.3233 | [5 empty] | 0.44129 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.4958
2023-05-01 | 5 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 36097.5959 | [5 empty] | 0.99608 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.5447
2023-06-01 | 6 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 19079.9566 | [5 empty] | 0.52649 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.9795
2023-07-01 | 7 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 18349.1888 | [5 empty] | 0.50633 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.8281
2023-08-01 | 8 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 19720.2276 | [5 empty] | 0.54416 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.9286
2023-09-01 | 9 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 17564.4547 | [5 empty] | 0.48467 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.5334
2023-10-01 | 10 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 17602.2571 | [5 empty] | 0.48572 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 4.0137
2023-11-01 | 11 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 15038.7905 | [5 empty] | 0.41498 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.0358
2023-12-01 | 12 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | 12772.7713 | [5 empty] | 0.35245 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.5625
2023-01-01 | 1 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 173779.684 |  |  | 15316.1903 | 25195.8444 |  | 5.3835 | 0 | 13.9061 | 2.7451 | 60.2931 | 0 | 66.5652 | 42.4031 |  | 169.2614 | EVC: Electric Meter (M) Usage minus Will's manual read for Clearwire,AT&T,Sprint,T-mobile |  | Cellular service electric use subtracted from electric meter | FALSE | FALSE | FALSE | Y | [84 empty] | 25195.8444
2023-02-01 | 2 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 159582.7143 |  |  | 14262.96 | 24879.0444 |  | 4.9437 | 0 | 12.9498 | 2.7106 | [6 empty] | EVC: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [84 empty] | 24879.0444
2023-03-01 | 3 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 160708.378 |  |  | 14067.9395 | 16787.4932 |  | 4.9785 | 0 | 12.7728 | 1.829 | [6 empty] | EVC: Chilled Water Usage (M) |  |  | FALSE | FALSE | FALSE | Y | [84 empty] | 16787.4932
2023-04-01 | 4 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 140557.0506 |  |  | 7323.0605 | 20839.8665 |  | 4.3543 | 0 | 6.6489 | 2.2706 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 20839.8665
2023-05-01 | 5 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 147382.7143 |  |  | 0 | 25230.737 |  | 4.5657 | 0 | 0 | 2.7489 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 25230.737
2023-06-01 | 6 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 151770.7143 |  |  | 0.0085714 | 23053.3464 |  | 4.7017 | 0 | 7.7823e-06 | 2.5117 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 23053.3464
2023-07-01 | 7 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 159050.2857 |  |  | 0.011429 | 45534.874 |  | 4.9272 | 0 | 1.0376e-05 | 4.9611 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 45534.874
2023-08-01 | 8 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 154454 |  |  | 0 | 68025.7502 |  | 4.7848 | 0 | 0 | 7.4116 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 68025.7502
2023-09-01 | 9 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 176071.4286 |  |  | 0 | 72539.287 |  | 5.4545 | 0 | 0 | 7.9033 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 72539.287
2023-10-01 | 10 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 186196.0714 |  |  | 40.57 | 37976.0178 |  | 5.7681 | 0 | 0.036835 | 4.1376 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 37976.0178
2023-11-01 | 11 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 167172.9653 |  |  | 9457.8016 | 10740.5417 |  | 5.1788 | 0 | 8.5871 | 1.1702 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 10740.5417
2023-12-01 | 12 | Provident Credit Union Event Center | Main campus | 110140 | Athletics | 169546.2933 |  |  | 12846.3705 | 18387.0153 |  | 5.2523 | 0 | 11.6637 | 2.0033 | [9 empty] | FALSE | FALSE | FALSE | Y | [84 empty] | 18387.0153
2023-01-01 | 1 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7617.2857 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 | Will's manual read for Clearwire,AT&T,Sprint,T-mobile |  |  | 0 | 0 | 0 | Y | [84 empty] | 25195.8444
2023-02-01 | 2 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7617.2857 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 24879.0444
2023-03-01 | 3 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7617.2857 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 16787.4932
2023-04-01 | 4 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7617.2857 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 20839.8665
2023-05-01 | 5 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7617.2857 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 25230.737
2023-06-01 | 6 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 5515 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 23053.3464
2023-07-01 | 7 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 8764 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 45534.874
2023-08-01 | 8 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7366 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 68025.7502
2023-09-01 | 9 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7680 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 72539.287
2023-10-01 | 10 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 8632.5 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 37976.0178
2023-11-01 | 11 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7394.5 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 10740.5417
2023-12-01 | 12 | Provident Credit Union Event Center-Cellular service | Main campus |  |  | 7969 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | Y | [84 empty] | 18387.0153
2023-01-01 | 1 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 812.72 |  | 49.5 |  |  |  | 0.32933 | 0.58789 | 0 | 0 | 5.8976 | 3.833 | 0 | 0 |  | 9.7306 | Reid-Hillview Airport: Electric (County of SC: 7856821607) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.52844 | 0.14567
2023-02-01 | 2 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1055.26 |  | 58.74 |  |  |  | 0.42762 | 0.69762 | 0 | 0 | [6 empty] | Reid-Hillview Airport: Gas (County of SC: 2866353030) Cost |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.72766 | 0.22001
2023-03-01 | 3 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1046.08 |  | 76.12 |  |  |  | 0.4239 | 0.90404 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.68532 | 0.26046
2023-04-01 | 4 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1683.24 |  | 67.76 |  |  |  | 0.68209 | 0.80475 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.0293 | 0.18299
2023-05-01 | 5 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1614.17 |  | 25.08 |  |  |  | 0.6541 | 0.29786 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.95378 | 0.044919
2023-06-01 | 6 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1850.69 |  | 8.8 |  |  |  | 0.74995 | 0.10451 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.1014 | 0.018472
2023-07-01 | 7 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 544.5 |  | 4.84 |  |  |  | 0.22065 | 0.057482 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.52554 | 0.01211
2023-08-01 | 8 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 859.38 |  | 0 |  |  |  | 0.34824 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.7727 | 0.0049462
2023-09-01 | 9 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1724.45 |  | 0 |  |  |  | 0.69879 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.1787 | 0.021056
2023-10-01 | 10 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1184.56 |  | 0.66 |  |  |  | 0.48001 | 0.0078385 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.91968 | 0.0059005
2023-11-01 | 11 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 1246 |  | 5.72 |  |  |  | 0.50491 | 0.067933 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.90291 | 0.017864
2023-12-01 | 12 | Reid Hillview Airport | Reid Hillview Airport | 8420 | Academic | 932.73 |  | 25.52 |  |  |  | 0.37797 | 0.30309 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.69641 | 0.068038
2018-01-01 | 1 | SC_Track & Field |  |  |  | 18.2623 | [5 empty] | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  | Not being considered | TRUE | TRUE | TRUE
2018-02-01 | 2 | SC_Track & Field |  |  |  | 201.9109 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-03-01 | 3 | SC_Track & Field |  |  |  | 2567.0349 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-04-01 | 4 | SC_Track & Field |  |  |  | 3354.2388 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-05-01 | 5 | SC_Track & Field |  |  |  | 3351.222 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-06-01 | 6 | SC_Track & Field |  |  |  | 3565.0656 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-07-01 | 7 | SC_Track & Field |  |  |  | 5046.8181 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-08-01 | 8 | SC_Track & Field |  |  |  | 5319.7411 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-09-01 | 9 | SC_Track & Field |  |  |  | 4652.906 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-10-01 | 10 | SC_Track & Field |  |  |  | 4807.7849 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-11-01 | 11 | SC_Track & Field |  |  |  | 1911.561 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2018-12-01 | 12 | SC_Track & Field |  |  |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-01-01 | 1 | Science | Main campus | 89180 | Academic | 26948.2793 |  |  | 5089.106 |  |  | 1.031 | 0 | 5.7066 | 0 | 21.8512 | 0 | 33.4443 | 0 |  | 55.2954 | Science: Electricity (M) Usage |  |  | FALSE | FALSE | TRUE | Y
2023-02-01 | 2 | Science | Main campus | 89180 | Academic | 41999.9361 |  |  | 0 |  |  | 1.6069 | 0 | 0 | 0 | [6 empty] | Will's Manual Data- Steam |  |  | FALSE | FALSE | TRUE | Y
2023-03-01 | 3 | Science | Main campus | 89180 | Academic | 48656.649 |  |  | 5097.732 |  |  | 1.8616 | 0 | 5.7162 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-04-01 | 4 | Science | Main campus | 89180 | Academic | 48143.4399 |  |  | 3852.196 |  |  | 1.842 | 0 | 4.3196 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-05-01 | 5 | Science | Main campus | 89180 | Academic | 51199.913 | [5 empty] | 1.9589 | 0 | 0 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-06-01 | 6 | Science | Main campus | 89180 | Academic | 51804.9263 |  |  | 0 |  |  | 1.982 | 0 | 0 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-07-01 | 7 | Science | Main campus | 89180 | Academic | 53895.0897 |  |  | 0.1174 |  |  | 2.062 | 0 | 0.00013164 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-08-01 | 8 | Science | Main campus | 89180 | Academic | 55091.4901 |  |  | 0 |  |  | 2.1078 | 0 | 0 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-09-01 | 9 | Science | Main campus | 89180 | Academic | 54775.235 |  |  | 109.4623 |  |  | 2.0957 | 0 | 0.12274 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-10-01 | 10 | Science | Main campus | 89180 | Academic | 53633.3455 |  |  | 5161.9871 |  |  | 2.052 | 0 | 5.7883 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-11-01 | 11 | Science | Main campus | 89180 | Academic | 43641.8464 |  |  | 5038.1892 |  |  | 1.6697 | 0 | 5.6495 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-12-01 | 12 | Science | Main campus | 89180 | Academic | 41337.4781 |  |  | 5476.8085 |  |  | 1.5816 | 0 | 6.1413 | 0 | [9 empty] | FALSE | FALSE | TRUE | Y
2023-01-01 | 1 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4620.5946 |  | 796.7 |  |  |  | 0.70084 | 3.5417 | 0 | 0 | #REF! | 17.2407 | 0 | 0 |  | #REF! | Simpkins Athletic: Electric (PG&E: 4147571902-1 / 4149482340) Usage |  | Negative | FALSE | TRUE | TRUE |  |  |  | solar to be added | 0.9226 | 2.6344
2023-02-01 | 2 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4186.8533 |  | 887.7258 |  |  |  | 0.63505 | 3.9463 | 0 | 0 | [6 empty] | Simpkins Athletic: Gas (PG&E: 4147571902-1 / 3037101005) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 0.082802 | 3.172
2023-03-01 | 3 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4162.9011 |  | 775.3411 |  |  |  | 0.63142 | 3.4467 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.084483 | 2.0638
2023-04-01 | 4 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4019.8052 |  | 397.4331 |  |  |  | 0.60972 | 1.7668 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.080837 | 0.78849
2023-05-01 | 5 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4109.6527 |  | 156.2333 |  |  |  | 0.62334 | 0.69452 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.082393 | 0.28206
2023-06-01 | 6 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4444.4334 |  | 39.5848 |  |  |  | 0.67412 | 0.17597 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.078697 | 0.10278
2023-07-01 | 7 | Simpkins Athletics Building | South campus | 22495 | Athletics | 4612.2232 |  | 8.1818 |  |  |  | 0.69957 | 0.036372 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.082689 | 0.052619
2023-08-01 | 8 | Simpkins Athletics Building | South campus | 22495 | Athletics | 5897.2368 |  | 0 |  |  |  | 0.89448 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.088851 | 0.039902
2023-09-01 | 9 | Simpkins Athletics Building | South campus | 22495 | Athletics | 5886.1085 |  | 0 |  |  |  | 0.89279 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.087258 | 0.039907
2023-10-01 | 10 | Simpkins Athletics Building | South campus | 22495 | Athletics | 6019.6851 |  | 42.4218 |  |  |  | 0.91305 | 0.18858 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.090475 | 0.135
2023-11-01 | 11 | Simpkins Athletics Building | South campus | 22495 | Athletics | 5695.3131 |  | 260.6427 |  |  |  | 0.86385 | 1.1587 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.088973 | 0.71804
2023-12-01 | 12 | Simpkins Athletics Building | South campus | 22495 | Athletics | 5301.2791 |  | 514.0323 |  |  |  | 0.80409 | 2.2851 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 7.3346 | 1.4489
2023-01-01 | 1 | Simpkins Center Storage Building | South campus | 768 | Storage | 88.7446 | [5 empty] | 0.39427 | 0 | 0 | 0 | 4.5741 | 0 | 0 | 0 |  | 4.5741 | Storage Electric (PG&E: 4147571902-1 / 4145273835) Usage |  | No heating/cooling in this building | FALSE | TRUE | TRUE |  |  |  |  | 0.034181
2023-02-01 | 2 | Simpkins Center Storage Building | South campus | 768 | Storage | 86.9948 | [5 empty] | 0.38649 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.036142
2023-03-01 | 3 | Simpkins Center Storage Building | South campus | 768 | Storage | 90.2683 | [5 empty] | 0.40104 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.035933
2023-04-01 | 4 | Simpkins Center Storage Building | South campus | 768 | Storage | 91.3033 | [5 empty] | 0.40563 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.037231
2023-05-01 | 5 | Simpkins Center Storage Building | South campus | 768 | Storage | 82.4039 | [5 empty] | 0.3661 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.034484
2023-06-01 | 6 | Simpkins Center Storage Building | South campus | 768 | Storage | 71.0507 | [5 empty] | 0.31566 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.033174
2023-07-01 | 7 | Simpkins Center Storage Building | South campus | 768 | Storage | 77.2261 | [5 empty] | 0.34309 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.035826
2023-08-01 | 8 | Simpkins Center Storage Building | South campus | 768 | Storage | 97.502 | [5 empty] | 0.43317 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.042387
2023-09-01 | 9 | Simpkins Center Storage Building | South campus | 768 | Storage | 84.0416 | [5 empty] | 0.37337 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | -0.00076806
2023-10-01 | 10 | Simpkins Center Storage Building | South campus | 768 | Storage | 93.6376 | [5 empty] | 0.416 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.026848
2023-11-01 | 11 | Simpkins Center Storage Building | South campus | 768 | Storage | 85.697 | [5 empty] | 0.38073 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.0379
2023-12-01 | 12 | Simpkins Center Storage Building | South campus | 768 | Storage | 80.6954 | [5 empty] | 0.35851 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 0.036983
2023-01-01 | 1 | Simpkins Stadium Center | South campus | 22203 | Office | 15144.1361 |  | 1373.0875 |  |  |  | 2.3272 | 6.1842 | 0 | 0 | 32.1152 | 51.8486 | 0 | 0 |  | 83.9638 | Simpkins Ctr: Gas (PG&E: 4147571902-1 / 9537109005) Usage |  | Negative | FALSE | TRUE | TRUE |  |  |  | solar to be added | 2.4522 | 4.5653
2023-02-01 | 2 | Simpkins Stadium Center | South campus | 22203 | Office | 14578.0516 |  | 1383.2847 |  |  |  | 2.2403 | 6.2302 | 0 | 0 | [6 empty] | Simpkins Ctr: Electric (PG&E: 4147571902-1 / 4149271279) Usage |  |  | FALSE | TRUE | TRUE |  |  |  |  | 2.4509 | 4.8972
2023-03-01 | 3 | Simpkins Stadium Center | South campus | 22203 | Office | 15173.8845 |  | 1423.5278 |  |  |  | 2.3318 | 6.4114 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.4366 | 3.6177
2023-04-01 | 4 | Simpkins Stadium Center | South campus | 22203 | Office | 14587.4027 |  | 1145.5 |  |  |  | 2.2417 | 5.1592 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.6009 | 2.2727
2023-05-01 | 5 | Simpkins Stadium Center | South campus | 22203 | Office | 14636.7023 |  | 719.3333 |  |  |  | 2.2493 | 3.2398 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.6629 | 1.178
2023-06-01 | 6 | Simpkins Stadium Center | South campus | 22203 | Office | 15829.0379 |  | 532.8788 |  |  |  | 2.4325 | 2.4 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.7645 | 0.93961
2023-07-01 | 7 | Simpkins Stadium Center | South campus | 22203 | Office | 16426.6285 |  | 572.1327 |  |  |  | 2.5243 | 2.5768 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.7221 | 1.0109
2023-08-01 | 8 | Simpkins Stadium Center | South campus | 22203 | Office | 23761.5996 |  | 565.3218 |  |  |  | 3.6515 | 2.5462 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 4.0325 | 1.0578
2023-09-01 | 9 | Simpkins Stadium Center | South campus | 22203 | Office | 22989.881 |  | 584.3333 |  |  |  | 3.5329 | 2.6318 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.8613 | 1.2461
2023-10-01 | 10 | Simpkins Stadium Center | South campus | 22203 | Office | 21685.4622 |  | 901.2482 |  |  |  | 3.3325 | 4.0591 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 3.3598 | 2.0696
2023-11-01 | 11 | Simpkins Stadium Center | South campus | 22203 | Office | 18505.1682 |  | 1164.0851 |  |  |  | 2.8437 | 5.2429 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.9859 | 3.0294
2023-12-01 | 12 | Simpkins Stadium Center | South campus | 22203 | Office | 15665.8885 |  | 1147.2121 |  |  |  | 2.4074 | 5.1669 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 2.5095 | 3.1838
2023-01-01 | 1 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE |  |  |  | needs to be calculated, Will said there is a model?
2023-02-01 | 2 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-03-01 | 3 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-04-01 | 4 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-05-01 | 5 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-06-01 | 6 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-07-01 | 7 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-08-01 | 8 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-09-01 | 9 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-10-01 | 10 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-11-01 | 11 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-12-01 | 12 | Spartan Athletic Center | South campus | 55234 | Office | [6 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | TRUE | TRUE
2023-01-01 | 1 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 119714.5909 |  |  | 31587.0975 | 3801.0383 |  | 3.3639 | 0 | 26.0135 | 0.37564 | 38.4342 | 0 | 170.4739 | 19.7817 |  | 228.6899 | SRAC Electric (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [89 empty] | 3801.0383
2023-02-01 | 2 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 113345.75 |  |  | 29049.4531 | 3699.7728 |  | 3.1849 | 0 | 23.9236 | 0.36563 | [6 empty] | SRAC Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [89 empty] | 3699.7728
2023-03-01 | 3 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 115561.1239 |  |  | 28763.7309 | 3075.859 |  | 3.2472 | 0 | 23.6883 | 0.30397 | [6 empty] | SRAC CHW (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [89 empty] | 3075.859
2023-04-01 | 4 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 113405.1261 |  |  | 17941.7378 | 7878.091 |  | 3.1866 | 0 | 14.7759 | 0.77856 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 7878.091
2023-05-01 | 5 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 114789.5 |  |  | 13205.0781 | 14006.4395 |  | 3.2255 | 0 | 10.875 | 1.3842 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 14006.4395
2023-06-01 | 6 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 106044.3571 |  |  | 8201.25 | 21896.1627 |  | 2.9798 | 0 | 6.7541 | 2.1639 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 21896.1627
2023-07-01 | 7 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 113135.1429 |  |  | 4881.6406 | 35118.4572 |  | 3.179 | 0 | 4.0203 | 3.4706 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 35118.4572
2023-08-01 | 8 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 120413.55 |  |  | 4396.6719 | 45108.4003 |  | 3.3836 | 0 | 3.6209 | 4.4579 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 45108.4003
2023-09-01 | 9 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 108200.325 |  |  | 8376.9609 | 27645.9801 |  | 3.0404 | 0 | 6.8988 | 2.7321 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 27645.9801
2023-10-01 | 10 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 120408.625 |  |  | 11863.3984 | 24451.6761 |  | 3.3834 | 0 | 9.7701 | 2.4165 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 24451.6761
2023-11-01 | 11 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 110973.3985 |  |  | 20983.1145 | 7379.6066 |  | 3.1183 | 0 | 17.2806 | 0.72929 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 7379.6066
2023-12-01 | 12 | Spartan Recreation and Aquatic Center | Main campus | 121426 | Athletics | 111802.5325 |  |  | 27749.496 | 6106.7352 |  | 3.1416 | 0 | 22.853 | 0.6035 | [9 empty] | FALSE | FALSE | FALSE | Y | [89 empty] | 6106.7352
2018-01-01 | 1 | SPX Central & east | Main Campus | 115492 | Athletics | 61362.75 |  |  | 747.7393 | 414.8324 |  | 1.8129 | 0 | 0.64744 | 0.043102 | 30.7164 | 0 | 5.8625 | 4.9028 |  | 41.4817 | SPXWest: Electric (M) Usage - Archived |  | Summed area : SPX central and east | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.35898
2018-02-01 | 2 | SPX Central & east | Main Campus | 115492 | Athletics | 76827 |  |  | 1518.3801 | 1455.2587 |  | 2.2697 | 0 | 1.3147 | 0.15121 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.28667
2018-03-01 | 3 | SPX Central & east | Main Campus | 115492 | Athletics | 86979.875 |  |  | 1607.8101 | 1825.9295 |  | 2.5697 | 0 | 1.3921 | 0.18972 | [6 empty] | SPXWest: Steam (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.13855
2018-04-01 | 4 | SPX Central & east | Main Campus | 115492 | Athletics | 102450.75 |  |  | 797.1301 | 2341.5618 |  | 3.0267 | 0 | 0.6902 | 0.2433 | [6 empty] | SPXWest: Chilled Water (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.021059
2018-05-01 | 5 | SPX Central & east | Main Campus | 115492 | Athletics | 97977 |  |  | 374.5203 | 3097.9323 |  | 2.8946 | 0 | 0.32428 | 0.32189 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.023583
2018-06-01 | 6 | SPX Central & east | Main Campus | 115492 | Athletics | 101428.75 |  |  | 73.02 | 5839.328 |  | 2.9965 | 0 | 0.063225 | 0.60673 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.024242
2018-07-01 | 7 | SPX Central & east | Main Campus | 115492 | Athletics | 105617 |  |  | 50 | 9496.2 |  | 3.1203 | 0 | 0.043293 | 0.98669 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.024242
2018-08-01 | 8 | SPX Central & east | Main Campus | 115492 | Athletics | 100121 |  |  | 100 | 8163.4 |  | 2.9579 | 0 | 0.086586 | 0.8482 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.025407
2018-09-01 | 9 | SPX Central & east | Main Campus | 115492 | Athletics | 87855 |  |  | 100 | 6330.8 |  | 2.5955 | 0 | 0.086586 | 0.65779 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.024723
2018-10-01 | 10 | SPX Central & east | Main Campus | 115492 | Athletics | 88599 |  |  | 170 | 6164.2 |  | 2.6175 | 0 | 0.1472 | 0.64048 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.024366
2018-11-01 | 11 | SPX Central & east | Main Campus | 115492 | Athletics | 74132 |  |  | 550 | 1749.3 |  | 2.1901 | 0 | 0.47622 | 0.18176 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.028785
2018-12-01 | 12 | SPX Central & east | Main Campus | 115492 | Athletics | 56363.2809 |  |  | 682.1178 | 307.1374 |  | 1.6652 | 0 | 0.59062 | 0.031913 | [9 empty] | FALSE | FALSE | FALSE | Y |  |  |  |  | 0.028574
2023-01-01 | 1 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 2124.1827 |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | SPX East: Steam (east) (M) Usage |  | only steam here, serves only the pool in the building | 0 | TRUE | TRUE | Y | [92 empty] | 210.5352
2023-02-01 | 2 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 2170.7031 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 213.0703
2023-03-01 | 3 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 2036.0253 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 198.5967
2023-04-01 | 4 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 1261.0352 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 127.2646
2023-05-01 | 5 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 927.2461 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 92.9375
2023-06-01 | 6 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 811.7076 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 80.7979
2023-07-01 | 7 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 719.7084 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 68.5117
2023-08-01 | 8 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 308.2677 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 32.4844
2023-09-01 | 9 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 268.3169 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 24.3809
2023-10-01 | 10 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 543.2397 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 49.3945
2023-11-01 | 11 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 1162.3625 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 112.1924
2023-12-01 | 12 | SPX East-Pool | Main Campus |  | Athletics |  |  |  | 1532.5756 |  |  | 0 | 0 | 0 | 0 | [9 empty] | 0 | TRUE | TRUE | Y | [92 empty] | 153.9883
2019-01-01 | 1 | Storage Building | South campus | 3135 | Storage | 3598.6235 | [5 empty] | 3.9166 | 0 | 0 | 0 | 54.7495 | 0 | 0 | 0 |  | 54.7495 | Housing: Block House Electric (Closed) (PG&E: 4147571902-1 / 8368689835) Usage |  |  | FALSE | TRUE | TRUE |  | G |  |  | 1.1273
2019-02-01 | 2 | Storage Building | South campus | 3135 | Storage | 3539.8026 | [5 empty] | 3.8526 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.238
2019-03-01 | 3 | Storage Building | South campus | 3135 | Storage | 3992.5255 | [5 empty] | 4.3453 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.2656
2019-04-01 | 4 | Storage Building | South campus | 3135 | Storage | 3691.6479 | [5 empty] | 4.0178 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.2506
2019-05-01 | 5 | Storage Building | South campus | 3135 | Storage | 3528.6717 | [5 empty] | 3.8405 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.1952
2019-06-01 | 6 | Storage Building | South campus | 3135 | Storage | 3535.9463 | [5 empty] | 3.8484 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.2527
2019-07-01 | 7 | Storage Building | South campus | 3135 | Storage | 4422.4287 | [5 empty] | 4.8132 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.5192
2019-08-01 | 8 | Storage Building | South campus | 3135 | Storage | 5257.2763 | [5 empty] | 5.7218 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.7902
2019-09-01 | 9 | Storage Building | South campus | 3135 | Storage | 5656.3381 | [5 empty] | 6.1561 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.9926
2019-10-01 | 10 | Storage Building | South campus | 3135 | Storage | 5177.9971 | [5 empty] | 5.6355 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.7622
2019-11-01 | 11 | Storage Building | South campus | 3135 | Storage | 4257.6198 | [5 empty] | 4.6338 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.4125
2019-12-01 | 12 | Storage Building | South campus | 3135 | Storage | 3645.878 | [5 empty] | 3.968 | 0 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE |  |  |  |  | 1.1615
2023-01-01 | 1 | Student Services Center | Main campus | 99853 | Office | 92265.6364 |  | 2307.4572 |  |  |  | 3.1527 | 2.3109 | 0 | 0 | 46.8056 | 17.3045 | 0 | 0 |  | 64.1101 | SSC: Main Electric (M) Usage |  |  | FALSE | TRUE | TRUE | Y |  |  |  |  | 7.5795 | [88 empty] | 29968.9394
2023-02-01 | 2 | Student Services Center | Main campus | 99853 | Office | 90699 |  | 2079.6054 |  |  |  | 3.0992 | 2.0827 | 0 | 0 | [6 empty] | SSC: Gas (PG&E: 9817802206-1 / 9817802005) Usage |  |  | FALSE | TRUE | TRUE | Y |  |  |  |  | 7.3111 | [88 empty] | 26566
2023-03-01 | 3 | Student Services Center | Main campus | 99853 | Office | 99974.83 |  | 2749.1833 |  |  |  | 3.4162 | 2.7532 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 6.7166 | [88 empty] | 28881.6593
2023-04-01 | 4 | Student Services Center | Main campus | 99853 | Office | 108658.67 |  | 2273.4028 |  |  |  | 3.7129 | 2.2767 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 4.53 | [88 empty] | 27422.3407
2023-05-01 | 5 | Student Services Center | Main campus | 99853 | Office | 126200 |  | 1283.5771 |  |  |  | 4.3123 | 1.2855 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 2.049 | [88 empty] | 29196
2023-06-01 | 6 | Student Services Center | Main campus | 99853 | Office | 119129.0854 |  | 974.2389 |  |  |  | 4.0707 | 0.97567 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 1.6571 | [88 empty] | 26113.1707
2023-07-01 | 7 | Student Services Center | Main campus | 99853 | Office | 141154.9146 |  | 1033.4063 |  |  |  | 4.8233 | 1.0349 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 1.7741 | [88 empty] | 27376.0793
2023-08-01 | 8 | Student Services Center | Main campus | 99853 | Office | 146382.8857 |  | 990.6207 |  |  |  | 5.0019 | 0.99208 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 1.792 | [88 empty] | 27874.5357
2023-09-01 | 9 | Student Services Center | Main campus | 99853 | Office | 122037.818 |  | 470.6696 |  |  |  | 4.1701 | 0.47136 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.97337 | [88 empty] | 27802.955
2023-10-01 | 10 | Student Services Center | Main campus | 99853 | Office | 121262.7963 |  | 338.8273 |  |  |  | 4.1436 | 0.33933 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 0.82228 | [88 empty] | 29214.2593
2023-11-01 | 11 | Student Services Center | Main campus | 99853 | Office | 103366.6696 |  | 1159.8178 |  |  |  | 3.5321 | 1.1615 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 3.0995 | [88 empty] | 28890.2336
2023-12-01 | 12 | Student Services Center | Main campus | 99853 | Office | 98644.9511 |  | 1618.2645 |  |  |  | 3.3707 | 1.6206 | 0 | 0 | [9 empty] | FALSE | TRUE | TRUE | Y |  |  |  |  | 4.4594 | [88 empty] | 29973.8095
2023-01-01 | 1 | Student Union | Main campus | 226256 | Office | 233848.4848 |  | 974.7 | 2408.0225 | 8472.5211 |  | 3.5265 | 0.4308 | 1.0643 | 0.44936 | 46.0525 | 6.3626 | 12.7409 | 18.4631 |  | 83.6192 | Student Union Electric Meter Cogen #1 (M) Usage |  | this building has many studing dining services | TRUE | TRUE | TRUE | Y |  | Y
2023-02-01 | 2 | Student Union | Main campus | 226257 | Office | 233799.5 |  | 1444.8489 | 2197.0264 | 8204.0738 |  | 3.5257 | 0.63859 | 0.97103 | 0.43512 | [6 empty] | Student Union Electric Meter Cogen #2 (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-03-01 | 3 | Student Union | Main campus | 226258 | Office | 258178.8799 |  | 1676.8511 | 2458.3301 | 9923.9539 |  | 3.8934 | 0.74112 | 1.0865 | 0.52633 | [6 empty] | Student Union PG&E: Gas (6400506178-9 / 6400506685) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-04-01 | 4 | Student Union | Main campus | 226259 | Office | 269621.7868 |  | 1664.4276 | 1761.8945 | 19430.8085 |  | 4.0659 | 0.73563 | 0.77871 | 1.0305 | [6 empty] | 2018-Student Union CHW Meter (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-05-01 | 5 | Student Union | Main campus | 226260 | Office | 257307.3333 |  | 1085.5474 | 2113.9941 | 31103.222 |  | 3.8802 | 0.47978 | 0.93432 | 1.6496 | [6 empty] | 2018-Student Union Steam Meter (M) Usage |  |  | TRUE | TRUE | TRUE | Y
2023-06-01 | 6 | Student Union | Main campus | 226261 | Office | 240170.4878 |  | 489.2056 | 2215.2539 | 23162.0238 |  | 3.6218 | 0.21621 | 0.97907 | 1.2284 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-07-01 | 7 | Student Union | Main campus | 226262 | Office | 255332.9884 |  | 347.5918 | 2100.2539 | 39600.2648 |  | 3.8504 | 0.15362 | 0.92824 | 2.1002 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-08-01 | 8 | Student Union | Main campus | 226263 | Office | 275927.2922 |  | 1061.2026 | 2581.709 | 91808.2702 |  | 4.1609 | 0.46901 | 1.141 | 4.8691 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-09-01 | 9 | Student Union | Main campus | 226264 | Office | 276750.1182 |  | 1703.625 | 2140.5957 | 45318.283 |  | 4.1733 | 0.75294 | 0.94606 | 2.4035 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-10-01 | 10 | Student Union | Main campus | 226265 | Office | 279557.8634 |  | 1845.3343 | 2780 | 52634.3047 |  | 4.2156 | 0.81556 | 1.2286 | 2.7915 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-11-01 | 11 | Student Union | Main campus | 226266 | Office | 242316.3485 |  | 1381.5407 | 2830 | 15134.2973 |  | 3.654 | 0.61058 | 1.2507 | 0.80265 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-12-01 | 12 | Student Union | Main campus | 226267 | Office | 231014.0765 |  | 720.9917 | 3240 | 3324.3533 |  | 3.4836 | 0.31865 | 1.4319 | 0.17631 | [9 empty] | TRUE | TRUE | TRUE | Y
2023-01-01 | 1 | Student Wellness Center | Main campus | 52700 | Office | 18817.2955 |  |  | 2273.7743 | 1904.5964 |  | 1.2183 | 0 | 4.3146 | 0.43368 | 15.005 | 0 | 27.6867 | 8.9511 |  | 51.6428 | SWC: Electric (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [95 empty] | 1904.5964
2023-02-01 | 2 | Student Wellness Center | Main campus | 52700 | Office | 17968 |  |  | 2212.6563 | 1514.49 |  | 1.1633 | 0 | 4.1986 | 0.34486 | [6 empty] | SWC: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [95 empty] | 1514.49
2023-03-01 | 3 | Student Wellness Center | Main campus | 52700 | Office | 19346.9554 |  |  | 1924.0319 | 2649.9044 |  | 1.2526 | 0 | 3.6509 | 0.60339 | [6 empty] | SWC: CHW (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [95 empty] | 2649.9044
2023-04-01 | 4 | Student Wellness Center | Main campus | 52700 | Office | 18978.1696 |  |  | 1179.386 | 3497.294 |  | 1.2287 | 0 | 2.2379 | 0.79635 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 3497.294
2023-05-01 | 5 | Student Wellness Center | Main campus | 52700 | Office | 19768.125 |  |  | 878.7305 | 4064.7797 |  | 1.2799 | 0 | 1.6674 | 0.92557 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 4064.7797
2023-06-01 | 6 | Student Wellness Center | Main campus | 52700 | Office | 18130.5976 |  |  | 550.2596 | 3816.7725 |  | 1.1738 | 0 | 1.0441 | 0.86909 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 3816.7725
2023-07-01 | 7 | Student Wellness Center | Main campus | 52700 | Office | 18982.5572 |  |  | 559.3977 | 4324.009 |  | 1.229 | 0 | 1.0615 | 0.98459 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 4324.009
2023-08-01 | 8 | Student Wellness Center | Main campus | 52700 | Office | 19745.9776 |  |  | 432.2775 | 4472.7492 |  | 1.2784 | 0 | 0.82026 | 1.0185 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 4472.7492
2023-09-01 | 9 | Student Wellness Center | Main campus | 52700 | Office | 19835.4837 |  |  | 513.4719 | 3924.0323 |  | 1.2842 | 0 | 0.97433 | 0.89352 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 3924.0323
2023-10-01 | 10 | Student Wellness Center | Main campus | 52700 | Office | 21283.7589 |  |  | 753.3824 | 3918.444 |  | 1.378 | 0 | 1.4296 | 0.89225 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 3918.444
2023-11-01 | 11 | Student Wellness Center | Main campus | 52700 | Office | 19397.0404 |  |  | 1357.0958 | 2947.967 |  | 1.2558 | 0 | 2.5751 | 0.67126 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 2947.967
2023-12-01 | 12 | Student Wellness Center | Main campus | 52700 | Office | 19505.593 |  |  | 1956.4328 | 2275.2955 |  | 1.2629 | 0 | 3.7124 | 0.51809 | [9 empty] | FALSE | FALSE | FALSE | Y | [95 empty] | 2275.2955
2023-01-01 | 1 | Sweeney Hall | Main campus | 101932 | Academic | 35129.2586 |  |  | 4.8865 | 523.9024 |  | 1.1759 | 0 | 0.0047939 | 0.061677 | 14.3182 | 0 | 0.028797 | 6.462 |  | 20.8089 | Sweeney Hall: Electricity (M) Usage |  |  | FALSE | TRUE | FALSE | Y | [99 empty] | 0.48865 |  | 36.5426 | 5.8999
2023-02-01 | 2 | Sweeney Hall | Main campus | 101932 | Academic | 35749 |  |  | 5.3778 | 759.3894 |  | 1.1966 | 0 | 0.0052759 | 0.0894 | [6 empty] | SH: Steam Rm 122 Usage (M) |  |  | FALSE | TRUE | FALSE | Y | [99 empty] | 0.53778 |  | 123.164 | 6.4758
2023-03-01 | 3 | Sweeney Hall | Main campus | 101932 | Academic | 35824.1346 |  |  | 4.1872 | 254.694 |  | 1.1992 | 0 | 0.0041079 | 0.029984 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.41872 |  | 207.9708
2023-04-01 | 4 | Sweeney Hall | Main campus | 101932 | Academic | 36180.3654 |  |  | 2.323 | 2504.3509 |  | 1.2111 | 0 | 0.002279 | 0.29483 | [6 empty] | Sweeney Hall: Chilled Water 1 (M) Usage |  |  | FALSE | TRUE | FALSE | Y | [99 empty] | 0.2323 |  | 1590.0326 | 14.1074
2023-05-01 | 5 | Sweeney Hall | Main campus | 101932 | Academic | 35503.5 |  |  | 1.6025 | 2958.2964 |  | 1.1884 | 0 | 0.0015721 | 0.34827 | [6 empty] | Sweeney Hall: Chilled Water 2 (M) Usage |  |  | FALSE | TRUE | FALSE | Y | [99 empty] | 0.16025 |  | 1994.7526 | 8.0615
2023-06-01 | 6 | Sweeney Hall | Main campus | 101932 | Academic | 32747.5714 |  |  | 1.0865 | 5871.6262 |  | 1.0962 | 0 | 0.0010659 | 0.69124 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.10865 |  | 3498.1511 | 23.6772
2023-07-01 | 7 | Sweeney Hall | Main campus | 101932 | Academic | 33376.9286 |  |  | 0.53681 | 11047.6189 |  | 1.1172 | 0 | 0.00052663 | 1.3006 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.053681 |  | 5508.1618 | 64.1299
2023-08-01 | 8 | Sweeney Hall | Main campus | 101932 | Academic | 33407.8429 |  |  | 0.42746 | 11687.476 |  | 1.1183 | 0 | 0.00041935 | 1.3759 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.042746 |  | 4254.1308 | 73.4175
2023-09-01 | 9 | Sweeney Hall | Main campus | 101932 | Academic | 36764.05 |  |  | 0.78687 | 10794.6133 |  | 1.2306 | 0 | 0.00077196 | 1.2708 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.078687 |  | 4088.4281 | 82.2705
2023-10-01 | 10 | Sweeney Hall | Main campus | 101932 | Academic | 40554.1071 |  |  | 1.6036 | 7115.8275 |  | 1.3575 | 0 | 0.0015732 | 0.83771 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.16036 |  | 3185.3206 | 39.7998
2023-11-01 | 11 | Sweeney Hall | Main campus | 101932 | Academic | 37783.6211 |  |  | 3.1886 | 1189.7701 |  | 1.2647 | 0 | 0.0031282 | 0.14007 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.31886 |  | 732.8549 | 11.437
2023-12-01 | 12 | Sweeney Hall | Main campus | 101932 | Academic | 34728.0858 |  |  | 3.3459 | 182.7883 |  | 1.1625 | 0 | 0.0032825 | 0.021519 | [9 empty] | FALSE | TRUE | FALSE | Y | [99 empty] | 0.33459 |  | 137.1602
2023-01-01 | 1 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 14832.8815 |  | 2117.7581 |  |  |  | 1.2867 | 0 | 5.3843 | 0 | 20.7689 | 39.4928 |  | 0 |  | 60.2617 | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Usage |  |  | FALSE | TRUE | TRUE | N |  |  |  |  | 6.9976 | [100 empty] | 5.8958 | 14832.8815 | 2117.7581
2023-02-01 | 2 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 19052.7331 |  | 2476.5484 |  |  |  | 1.6528 | 0 | 6.2965 | 0 | [6 empty] | WSH: NatGas (PG&E: 4564269832-3 / 4564269015) Usage |  |  | FALSE | TRUE | TRUE | N |  |  |  |  | 8.8052 | [100 empty] | 7.7117 | 19052.7331 | 2476.5484
2023-03-01 | 3 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 20003.2768 |  | 2426.3977 |  |  |  | 1.7353 | 0 | 6.169 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 6.3735 | [100 empty] | 7.3885 | 20003.2768 | 2426.3977
2023-04-01 | 4 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 19028.3371 |  | 1837.8896 |  |  |  | 1.6507 | 0 | 4.6728 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 3.3527 | [100 empty] | 8.0186 | 19028.3371 | 1837.8896
2023-05-01 | 5 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 17401.797 |  | 1365.7127 |  |  |  | 1.5096 | 0 | 3.4723 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 2.1655 | [100 empty] | 7.3522 | 17401.797 | 1365.7127
2023-06-01 | 6 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 11922.8375 |  | 662.2935 |  |  |  | 1.0343 | 0 | 1.6839 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 1.1387 | [100 empty] | 5.3058 | 11922.8375 | 662.2935
2023-07-01 | 7 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 14108.9892 |  | 244.6419 |  |  |  | 1.2239 | 0 | 0.62199 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 0.46887 | [100 empty] | 6.8042 | 14108.9892 | 244.6419
2023-08-01 | 8 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 27071.464 |  | 282.6774 |  |  |  | 2.3484 | 0 | 0.7187 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 0.56259 | [100 empty] | 12.2074 | 27071.464 | 282.6774
2023-09-01 | 9 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 32593.7637 |  | 420.5462 |  |  |  | 2.8275 | 0 | 1.0692 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 0.91522 | [100 empty] | 14.2447 | 32593.7637 | 420.5462
2023-10-01 | 10 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 28446.4133 |  | 810.2291 |  |  |  | 2.4677 | 0 | 2.06 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 1.8528 | [100 empty] | 11.7463 | 28446.4133 | 810.2291
2023-11-01 | 11 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 19776.7044 |  | 1414.0634 |  |  |  | 1.7156 | 0 | 3.5952 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 3.7051 | [100 empty] | 8.2804 | 19776.7044 | 1414.0634
2023-12-01 | 12 | Washburn Hall (Student Residence) | Main campus | 39332 | Residential | 15175.8854 |  | 1474.5419 |  |  |  | 1.3165 | 0 | 3.749 | 0 | [9 empty] | FALSE | TRUE | TRUE | N |  |  |  |  | 4.0667 | [100 empty] | 6.2843 | 15175.8854 | 1474.5419
2023-01-01 | 1 | Washington Square Hall | Main campus | 71857 | Academic | 46348.2676 |  |  | 3364.5566 | 2042.4901 |  | 2.2008 | 0 | 4.6823 | 0.34109 | 45.6115 | 0 | 33.9486 | 23.9282 |  | 103.4883 | Washington Square Hall : Electricity (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-02-01 | 2 | Washington Square Hall | Main campus | 71857 | Academic | 71099.9966 |  |  | 2587.87 | 855.366 |  | 3.3761 | 0 | 3.6014 | 0.14284 | [6 empty] | Washington Square Hall : Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-03-01 | 3 | Washington Square Hall | Main campus | 71857 | Academic | 80123.738 |  |  | 2694.7229 | 616.2 |  | 3.8045 | 0 | 3.7501 | 0.1029 | [6 empty] | Washington Square Hall : Chilled Water (M) Usage |  |  | FALSE | FALSE | FALSE | Y
2023-04-01 | 4 | Washington Square Hall | Main campus | 71857 | Academic | 82076.2361 |  |  | 2013.2071 | 4007.1791 |  | 3.8972 | 0 | 2.8017 | 0.66919 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-05-01 | 5 | Washington Square Hall | Main campus | 71857 | Academic | 87100.029 |  |  | 1764.64 | 9035.2178 |  | 4.1358 | 0 | 2.4558 | 1.5089 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-06-01 | 6 | Washington Square Hall | Main campus | 71857 | Academic | 83853.6169 |  |  | 1154.422 | 10410.1026 |  | 3.9816 | 0 | 1.6066 | 1.7385 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-07-01 | 7 | Washington Square Hall | Main campus | 71857 | Academic | 87146.3869 |  |  | 722.353 | 11966.0684 |  | 4.138 | 0 | 1.0053 | 1.9983 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-08-01 | 8 | Washington Square Hall | Main campus | 71857 | Academic | 87597.0023 |  |  | 11.5896 | 19501.0131 |  | 4.1594 | 0 | 0.016129 | 3.2566 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-09-01 | 9 | Washington Square Hall | Main campus | 71857 | Academic | 90265.8185 |  |  | 354.2384 | 19965.4285 |  | 4.2861 | 0 | 0.49298 | 3.3342 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-10-01 | 10 | Washington Square Hall | Main campus | 71857 | Academic | 91037.0968 |  |  | 1386.052 | 21697.2081 |  | 4.3227 | 0 | 1.9289 | 3.6234 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-11-01 | 11 | Washington Square Hall | Main campus | 71857 | Academic | 77191.4623 |  |  | 3952.953 | 20964.2175 |  | 3.6653 | 0 | 5.5011 | 3.501 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-12-01 | 12 | Washington Square Hall | Main campus | 71857 | Academic | 76742.9836 |  |  | 4387.8367 | 22223.4934 |  | 3.644 | 0 | 6.1063 | 3.7113 | [9 empty] | FALSE | FALSE | FALSE | Y
2023-01-01 | 1 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 32096.1638 |  |  | 1867.6502 | 911.8962 |  | 1.4246 | 0 | 2.4296 | 0.14235 | 17.7018 | 0 | 11.3418 | 9.2171 |  | 38.2607 | Uchida Hall: Electricity (M) Usage |  | 2018 CHW data considered cause 2023 data quality is poor | FALSE | FALSE | FALSE | Y |  | Y | [110 empty] | 0 |  | 190.4023
2023-02-01 | 2 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 30498.5 |  |  | 1639.2969 | 1209.5176 |  | 1.3537 | 0 | 2.1325 | 0.18881 | [6 empty] | Uchida Hall: Steam (M) Usage |  |  | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 160.4805
2023-03-01 | 3 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 33840.0521 |  |  | 806.5195 | 1798.8205 |  | 1.502 | 0 | 1.0492 | 0.28081 | [6 empty] | 2018 : YUH: CHW (M) Usage - Archived |  |  | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 84.7998
2023-04-01 | 4 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 33463.1979 |  |  | 453.6758 | 2971.4548 |  | 1.4853 | 0 | 0.59018 | 0.46386 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 41.4355
2023-05-01 | 5 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 32042.5 |  |  | 402.9004 | 4213.5686 |  | 1.4222 | 0 | 0.52413 | 0.65776 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 40.5928
2023-06-01 | 6 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 30012.0714 |  |  | 158.3873 | 3189.2861 |  | 1.3321 | 0 | 0.20604 | 0.49787 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 17.0625
2023-07-01 | 7 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 31897.4286 |  |  | 107.3744 | 7407.8038 |  | 1.4158 | 0 | 0.13968 | 1.1564 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0.00097656 |  | 9.0371
2023-08-01 | 8 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 34108.35 |  |  | 60.1317 | 16542.3556 |  | 1.5139 | 0 | 0.078224 | 2.5824 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 7.6008 |  | 5.3262
2023-09-01 | 9 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 33517.2333 |  |  | 97.5665 | 9124.5455 |  | 1.4877 | 0 | 0.12692 | 1.4244 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 9.5469
2023-10-01 | 10 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 36419.6667 |  |  | 100.9834 | 8997.3898 |  | 1.6165 | 0 | 0.13137 | 1.4045 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 9.8047
2023-11-01 | 11 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 34967.3285 |  |  | 1069.6306 | 2063.0253 |  | 1.5521 | 0 | 1.3915 | 0.32205 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 98.166
2023-12-01 | 12 | Yoshihiro Uchida Hall | Main campus | 76871 | Athletics | 35951.9646 |  |  | 1954.4602 | 614.2747 |  | 1.5958 | 0 | 2.5425 | 0.095892 | [9 empty] | FALSE | FALSE | FALSE | Y | [112 empty] | 0 |  | 198.9971
2023-01-01 | 1 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 29968.94 | [5 empty] | 0.17606 | 0 | 0 | 0 | 1.9932 |  |  |  |  | 1.9932 |  |  |  | FALSE | 0 | 0 | Y
2023-02-01 | 2 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 26566 | [5 empty] | 0.15607 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-03-01 | 3 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 28881.66 | [5 empty] | 0.16967 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-04-01 | 4 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 27422.34 | [5 empty] | 0.1611 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-05-01 | 5 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 29196 | [5 empty] | 0.17152 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-06-01 | 6 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 26113.17 | [5 empty] | 0.15341 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-07-01 | 7 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 27376.08 | [5 empty] | 0.16083 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-08-01 | 8 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 27874.54 | [5 empty] | 0.16376 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-09-01 | 9 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 27802.96 | [5 empty] | 0.16334 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-10-01 | 10 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 29214.26 | [5 empty] | 0.17163 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-11-01 | 11 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 28890.23 | [5 empty] | 0.16973 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-12-01 | 12 | NORTH PARKING FACILITY | Main campus | 580783 | Parking | 29973.81 | [5 empty] | 0.17609 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-01-01 | 1 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 42981.89 | [5 empty] | 0.23475 | 0 | 0 | 0 | 2.6696 | [8 empty] | FALSE | 0 | 0 | Y
2023-02-01 | 2 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 38842.5 | [5 empty] | 0.21214 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-03-01 | 3 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 42518.67 | [5 empty] | 0.23222 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-04-01 | 4 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 40050.83 | [5 empty] | 0.21874 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-05-01 | 5 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 40490 | [5 empty] | 0.22114 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-06-01 | 6 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 39108 | [5 empty] | 0.21359 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-07-01 | 7 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 40608.5 | [5 empty] | 0.22178 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-08-01 | 8 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 40522.76 | [5 empty] | 0.22132 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-09-01 | 9 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 39782.26 | [5 empty] | 0.21727 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-10-01 | 10 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 41365.98 | [5 empty] | 0.22592 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-11-01 | 11 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 40423.28 | [5 empty] | 0.22077 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-12-01 | 12 | SOUTH PARKING FACILITY | Main campus | 624735 | Parking | 42111.41 | [5 empty] | 0.22999 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-01-01 | 1 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 10574.45 | [5 empty] | 0.11158 | 0 | 0 | 0 | 2.2423 | [8 empty] | FALSE | 0 | 0 | Y
2023-02-01 | 2 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 16371 | [5 empty] | 0.17275 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-03-01 | 3 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 17487.04 | [5 empty] | 0.18452 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-04-01 | 4 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 17176.46 | [5 empty] | 0.18125 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-05-01 | 5 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 17758.75 | [5 empty] | 0.18739 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-06-01 | 6 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 17112 | [5 empty] | 0.18057 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-07-01 | 7 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 19265 | [5 empty] | 0.20328 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-08-01 | 8 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 19332.71 | [5 empty] | 0.204 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-09-01 | 9 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 19164.64 | [5 empty] | 0.20223 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-10-01 | 10 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 19382.41 | [5 empty] | 0.20452 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-11-01 | 11 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 18863.29 | [5 empty] | 0.19905 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-12-01 | 12 | WEST PARKING FACILITY | Main campus | 323350 | Parking | 20012.75 | [5 empty] | 0.21118 | 0 | 0 | 0 | [9 empty] | FALSE | 0 | 0 | Y
2023-01-01 | 1 | San Antonio Parking Lot | Main campus |  | Parking | 3110 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-02-01 | 2 | San Antonio Parking Lot | Main campus |  | Parking | 6240 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-03-01 | 3 | San Antonio Parking Lot | Main campus |  | Parking | 5260 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-04-01 | 4 | San Antonio Parking Lot | Main campus |  | Parking | 5780 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-05-01 | 5 | San Antonio Parking Lot | Main campus |  | Parking | 5300 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-06-01 | 6 | San Antonio Parking Lot | Main campus |  | Parking | 2270 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-07-01 | 7 | San Antonio Parking Lot | Main campus |  | Parking | 2280 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-08-01 | 8 | San Antonio Parking Lot | Main campus |  | Parking | 3760 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-09-01 | 9 | San Antonio Parking Lot | Main campus |  | Parking | 4960 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-10-01 | 10 | San Antonio Parking Lot | Main campus |  | Parking | 5590 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-11-01 | 11 | San Antonio Parking Lot | Main campus |  | Parking | 4920 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-12-01 | 12 | San Antonio Parking Lot | Main campus |  | Parking | 3190 | [5 empty] | 0 | 0 | 0 | 0 | [9 empty] | TRUE | 0 | 0 | Y
2023-01-01 | 1 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 13252.1899
2023-02-01 | 2 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 12923.7588
2023-03-01 | 3 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 13716.6104
2023-04-01 | 4 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 14864.3485
2023-05-01 | 5 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 14598.6487
2023-06-01 | 6 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 7917.4792
2023-07-01 | 7 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 11612.4765
2023-08-01 | 8 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 13006.6212
2023-09-01 | 9 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 15101.9471
2023-10-01 | 10 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 15937.5754
2023-11-01 | 11 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 14652.3424
2023-12-01 | 12 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Garage | 13854.3428
|  | Computer Center | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Computer Center | [19 empty] | Chilled Water usage data was missing and has been calculated based on metered data
|  | Faculty Office Building | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Faculty Office Building | [19 empty] | Steam usage data was missing and has been calculated based on metered data
|  | Faculty Office Building | [19 empty] | Chilled Water usage data was missing and has been calculated based on metered data
|  | Morris Dailey Auditorium | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Morris Dailey Auditorium | [19 empty] | Steam usage data was missing and has been calculated based on metered data
|  | Spartan Memorial | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Tower Hall | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Tower Hall | [19 empty] | Steam usage data was missing and has been calculated based on metered data
|  | UPD Building | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | UPD Building | [19 empty] | Steam usage data was missing and has been calculated based on metered data
|  | UPD Building | [19 empty] | Chilled Water usage data was missing and has been calculated based on metered data
| weather normalised | 4th Street Building | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
| doubtful data | 4th Street Building | [19 empty] | Gas usage data was missing and has been calculated based on metered data
red text | summed areas -combined bldgs or averaged months | Baseball Batting Structure | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Modular Building A | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Modular Building B | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Modular Building C | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | President's House | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | President's House | [19 empty] | Gas usage data was missing and has been calculated based on metered data
|  | Softball & Tennis Facility | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | South Campus Parking Structure | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Spartan Athletic Center | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
|  | Training/Locker Facility | [19 empty] | Electricity usage data was missing and has been calculated based on metered data
Note on G87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Come from split meter
Note on F243: Marya Thawer: 15% lecture, 27% faculty office
Note on F399: Marya Thawer: Could be residential
Note on F663: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Office
Note on J663: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Taken from 2018
Note on C771: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does this exist? Reply: Will thinks this is referring to lot 4

## Missing Bldgs - Monthly EUI
[5 empty] | Calculated energy |  |  |  | EUI(kBtu/sq.ft)
Month | Building Name | Campus Center | Area | Building Use Type | Electricity 1 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Electric EUI | Gas EUI | Steam EUI | CHW EUI | Total EUI | List of meter names
1 | Administration | Main campus | 39323 | Office |  |  | 1696.6153 | 1421.1469 |  |  | 27.6867 | 8.9511
2 | Administration | Main campus | 39323 | Office |  |  | 1651.011 | 1130.0624
3 | Administration | Main campus | 39323 | Office |  |  | 1435.6491 | 1977.2712
4 | Administration | Main campus | 39323 | Office |  |  | 880.0189 | 2609.5653
5 | Administration | Main campus | 39323 | Office |  |  | 655.6797 | 3033.0044
6 | Administration | Main campus | 39323 | Office |  |  | 410.5856 | 2847.9496
7 | Administration | Main campus | 39323 | Office |  |  | 417.4041 | 3226.4327
8 | Administration | Main campus | 39323 | Office |  |  | 322.5512 | 3337.4178
9 | Administration | Main campus | 39323 | Office |  |  | 383.1358 | 2927.9834
10 | Administration | Main campus | 39323 | Office |  |  | 562.1491 | 2923.8135
11 | Administration | Main campus | 39323 | Office |  |  | 1012.6201 | 2199.6757
12 | Administration | Main campus | 39323 | Office |  |  | 1459.8256 | 1697.7503
1 | Computer Center | Main campus | 12900 | Data Center | 67059.4503 |  |  | 11646.861 | 399.4756 |  |  | 504.5753 |  |  | 0.45 | 82.431 | 744 | 61328.664 | 61328.664
2 | Computer Center | Main campus | 12900 | Data Center | 167616.7434 |  |  | 49505.2339 | [6 empty] | 0.45 | 82.431 | 672 | 55393.632 | 55393.632
3 | Computer Center | Main campus | 12900 | Data Center | 186019.5491 |  |  | 59158.9925 | [6 empty] | 0.45 | 82.431 | 744 | 61328.664 | 61328.664
4 | Computer Center | Main campus | 12900 | Data Center | 140514.2282 |  |  | 47644.3137 | [6 empty] | 0.55 | 100.749 | 720 | 72539.28 | 72539.28
5 | Computer Center | Main campus | 12900 | Data Center | 105188.5716 |  |  | 36681.6815 | [6 empty] | 0.55 | 100.749 | 744 | 74957.256 | 74957.256
6 | Computer Center | Main campus | 12900 | Data Center | 62896.0751 |  |  | 27062.4737 | [6 empty] | 0.55 | 100.749 | 720 | 72539.28 | 72539.28
7 | Computer Center | Main campus | 12900 | Data Center | 64810.9697 |  |  | 29552.7436 | [6 empty] | 0.55 | 100.749 | 744 | 74957.256 | 74957.256
8 | Computer Center | Main campus | 12900 | Data Center | 104945.7384 |  |  | 46418.2718 | [6 empty] | 0.6 | 109.908 | 744 | 81771.552 | 81771.552
9 | Computer Center | Main campus | 12900 | Data Center | 178732.6039 |  |  | 90346.5081 | [6 empty] | 0.55 | 100.749 | 720 | 72539.28 | 72539.28
10 | Computer Center | Main campus | 12900 | Data Center | 184522.2165 |  |  | 80027.8455 | [6 empty] | 0.45 | 82.431 | 744 | 61328.664 | 61328.664
11 | Computer Center | Main campus | 12900 | Data Center | 141452.5898 |  |  | 42004.6589 | [6 empty] | 0.45 | 82.431 | 720 | 59350.32 | 59350.32
12 | Computer Center | Main campus | 12900 | Data Center | 106568.2715 |  |  | 22368.8246 | [6 empty] | 0.45 | 82.431 | 744 | 61328.664 | 61328.664
1 | Corporation Yard Offices | Main campus | 42019 | Office | 28733.929 |  |  |  | 26.9575
2 | Corporation Yard Offices | Main campus | 42019 | Office | 27294.3904
3 | Corporation Yard Offices | Main campus | 42019 | Office | 28746.8339
4 | Corporation Yard Offices | Main campus | 42019 | Office | 28560.931
5 | Corporation Yard Offices | Main campus | 42019 | Office | 27242.9811
6 | Corporation Yard Offices | Main campus | 42019 | Office | 26270.2062
7 | Corporation Yard Offices | Main campus | 42019 | Office | 27156.5771
8 | Corporation Yard Offices | Main campus | 42019 | Office | 28957.4601
9 | Corporation Yard Offices | Main campus | 42019 | Office | 27324.9701
10 | Corporation Yard Offices | Main campus | 42019 | Office | 27098.0429
11 | Corporation Yard Offices | Main campus | 42019 | Office | 26255.8658
12 | Corporation Yard Offices | Main campus | 42019 | Office | 28341.0838
1 | Faculty Office Building | Main campus | 16496 | Office | 11280.4896 |  | 711.7302 | 596.1712 | 26.9575 |  | 27.6867 | 8.9511 | 63.5953
2 | Faculty Office Building | Main campus | 16496 | Office | 10715.3494 |  | 692.5992 | 474.0612
3 | Faculty Office Building | Main campus | 16496 | Office | 11285.5559 |  | 602.2548 | 829.4653
4 | Faculty Office Building | Main campus | 16496 | Office | 11212.5733 |  | 369.168 | 1094.7127
5 | Faculty Office Building | Main campus | 16496 | Office | 10695.1669 |  | 275.0576 | 1272.3455
6 | Faculty Office Building | Main campus | 16496 | Office | 10313.2707 |  | 172.2407 | 1194.715
7 | Faculty Office Building | Main campus | 16496 | Office | 10661.246 |  | 175.101 | 1353.4887
8 | Faculty Office Building | Main campus | 16496 | Office | 11368.2444 |  | 135.3102 | 1400.0469
9 | Faculty Office Building | Main campus | 16496 | Office | 10727.3545 |  | 160.7255 | 1228.2891
10 | Faculty Office Building | Main campus | 16496 | Office | 10638.2664 |  | 235.8216 | 1226.5399
11 | Faculty Office Building | Main campus | 16496 | Office | 10307.6409 |  | 424.7942 | 922.764
12 | Faculty Office Building | Main campus | 16496 | Office | 11126.2648 |  | 612.3969 | 712.2063 | [9 empty] | Steam(therms)
1 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 11778.6026 |  | 93.541 |  | 68.1406 |  | 4.3701 |  | 72.5107 |  |  |  |  | 93.541
2 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 10915.191 |  | 68.1227 | [10 empty] | 68.1227
3 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 13095.6922 |  | 34.4976 | [10 empty] | 34.4976
4 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 14364.5313 |  | 15.5619 | [10 empty] | 15.5619
5 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 16006.4719 |  | 3.6114 | [10 empty] | 3.6114
6 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 14172.7537 |  | 0.79805 | [10 empty] | 0.79805
7 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 15606.916 |  | 18.0804 | [10 empty] | 18.0804
8 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 16009.2394 |  | 9.687 | [10 empty] | 9.687
9 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 14796.6724 |  | 5.9988 | [10 empty] | 5.9988
10 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 15720.3147 |  | 11.7822 | [10 empty] | 11.7822
11 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 14326.6429 |  | 39.7184 | [10 empty] | 39.7184
12 | Morris Dailey Auditorium | Main campus | 8545 | Theater | 13858.1059 |  | 72.0214 | [10 empty] | 72.0214 | Month | CHW Total[kBtu/sf] | CHW(tons) | HHW total
1 | Spartan Memorial | Main campus | 2300 | Theater | 3170.367 |  |  |  | 68.1406 |  |  |  | 68.1406 |  |  |  |  | 25.1778 | 1 | 0.35151 | 16.8433 | 1.0947
2 | Spartan Memorial | Main campus | 2300 | Theater | 2937.9683 | [12 empty] | 18.3361 | 2 | 0.31292 | 14.9939 | 0.79722
3 | Spartan Memorial | Main campus | 2300 | Theater | 3524.8791 | [12 empty] | 9.2855 | 3 | 0.48049 | 23.0235 | 0.40372
4 | Spartan Memorial | Main campus | 2300 | Theater | 3866.404 | [12 empty] | 4.1887 | 4 | 0.1701 | 8.1506 | 0.18212
5 | Spartan Memorial | Main campus | 2300 | Theater | 4308.354 | [12 empty] | 0.97205 | 5 | 0.52032 | 24.9321 | 0.042263
6 | Spartan Memorial | Main campus | 2300 | Theater | 3814.7845 | [12 empty] | 0.21481 | 6 | 0.69555 | 33.3284 | 0.0093394
7 | Spartan Memorial | Main campus | 2300 | Theater | 4200.8083 | [12 empty] | 4.8666 | 7 | 1.7826 | 85.4145 | 0.21159
8 | Spartan Memorial | Main campus | 2300 | Theater | 4309.099 | [12 empty] | 2.6074 | 8 | 2.1698 | 103.9686 | 0.11336
9 | Spartan Memorial | Main campus | 2300 | Theater | 3982.7205 | [12 empty] | 1.6147 | 9 | 1.2461 | 59.711 | 0.070202
10 | Spartan Memorial | Main campus | 2300 | Theater | 4231.331 | [12 empty] | 3.1713 | 10 | 1.0671 | 51.1333 | 0.13788
11 | Spartan Memorial | Main campus | 2300 | Theater | 3856.2058 | [12 empty] | 10.6907 | 11 | 0.29682 | 14.2228 | 0.46481
12 | Spartan Memorial | Main campus | 2300 | Theater | 3730.0929 | [12 empty] | 19.3855 | 12 | 0.22479 | 10.7714 | 0.84285
1 | Tower Hall | Main campus | 13096 | Theater | 18051.794 |  | 143.3602 |  | 68.1406 |  | 4.3701 | [6 empty] | 143.3602
2 | Tower Hall | Main campus | 13096 | Theater | 16728.5361 |  | 104.4042 | [10 empty] | 104.4042
3 | Tower Hall | Main campus | 13096 | Theater | 20070.3551 |  | 52.8708 | [10 empty] | 52.8708
4 | Tower Hall | Main campus | 13096 | Theater | 22014.968 |  | 23.85 | [10 empty] | 23.85
5 | Tower Hall | Main campus | 13096 | Theater | 24531.3933 |  | 5.5348 | [10 empty] | 5.5348
6 | Tower Hall | Main campus | 13096 | Theater | 21721.0511 |  | 1.2231 | [10 empty] | 1.2231
7 | Tower Hall | Main campus | 13096 | Theater | 23919.0371 |  | 27.7099 | [10 empty] | 27.7099
8 | Tower Hall | Main campus | 13096 | Theater | 24535.6348 |  | 14.8463 | [10 empty] | 14.8463
9 | Tower Hall | Main campus | 13096 | Theater | 22677.264 |  | 9.1937 | [10 empty] | 9.1937
10 | Tower Hall | Main campus | 13096 | Theater | 24092.831 |  | 18.0573 | [10 empty] | 18.0573
11 | Tower Hall | Main campus | 13096 | Theater | 21956.9006 |  | 60.8721 | [10 empty] | 60.8721
12 | Tower Hall | Main campus | 13096 | Theater | 21238.8245 |  | 110.3795 | [10 empty] | 110.3795
1 | UPD Building | Main campus | 25391 | Office | 17363.1736 |  | 1095.5105 | 917.6396 | 26.9575 |  | 27.6867 | 8.9511 | 63.5953
2 | UPD Building | Main campus | 25391 | Office | 16493.2975 |  | 1066.0637 | 729.6853
3 | UPD Building | Main campus | 25391 | Office | 17370.9717 |  | 927.0037 | 1276.731
4 | UPD Building | Main campus | 25391 | Office | 17258.6353 |  | 568.2313 | 1685.0055
5 | UPD Building | Main campus | 25391 | Office | 16462.2322 |  | 423.3747 | 1958.4217
6 | UPD Building | Main campus | 25391 | Office | 15874.4093 |  | 265.1165 | 1838.9311
7 | UPD Building | Main campus | 25391 | Office | 16410.0204 |  | 269.5193 | 2083.319
8 | UPD Building | Main campus | 25391 | Office | 17498.2477 |  | 208.2724 | 2154.9825
9 | UPD Building | Main campus | 25391 | Office | 16511.776 |  | 247.3921 | 1890.6092
10 | UPD Building | Main campus | 25391 | Office | 16374.6497 |  | 362.9816 | 1887.9167
11 | UPD Building | Main campus | 25391 | Office | 15865.7438 |  | 653.8524 | 1420.3384
12 | UPD Building | Main campus | 25391 | Office | 17125.7874 |  | 942.6145 | 1096.2434
1 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 3280.486 |  |  |  | 29.0632
2 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 2280.9483
3 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 3101.0817
4 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 2102.7321
5 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 1750.4612
6 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 790.1195
7 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 658.1711
8 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 296.8129
9 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 554.1246
10 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 1398.2038
11 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 2719.886
12 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 2374.6883
1 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 13543.4201 | 1228.0052 |  |  | 32.1138 |  | 0 |  | 32.1138
2 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 13037.17 | 1237.1249
3 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 13570.0241 | 1273.1159
4 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 13045.5327 | 1024.4649
5 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 13089.6214 | 643.3276
6 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 14155.9286 | 476.5741
7 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 14690.3547 | 511.6804
8 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 21250.0286 | 505.5891
9 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 20559.8797 | 522.5919
10 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 19393.3363 | 806.0211
11 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 16549.1953 | 1041.0863
12 | 4th Street Building | Off Campus 4th Street | 19857 | Office | 14010.0239 | 1025.9961
1 | Bally Hut | South campus | 342 | Infrastructure | #VALUE! |  |  |  | #VALUE! |  | 0 |  | #VALUE!
2 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
3 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
4 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
5 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
6 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
7 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
8 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
9 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
10 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
11 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
12 | Bally Hut | South campus | 342 | Infrastructure | #VALUE!
1 | Baseball Batting Structure | South campus | 9030 | Athletics | 5031.2583 |  |  |  | 26.9413 | 0 |  |  | 26.9413
2 | Baseball Batting Structure | South campus | 9030 | Athletics | 4860.858
3 | Baseball Batting Structure | South campus | 9030 | Athletics | 5431.9296
4 | Baseball Batting Structure | South campus | 9030 | Athletics | 4951.9701
5 | Baseball Batting Structure | South campus | 9030 | Athletics | 5013.1913
6 | Baseball Batting Structure | South campus | 9030 | Athletics | 5421.5761
7 | Baseball Batting Structure | South campus | 9030 | Athletics | 5626.2558
8 | Baseball Batting Structure | South campus | 9030 | Athletics | 7536.4576
9 | Baseball Batting Structure | South campus | 9030 | Athletics | 7534.565
10 | Baseball Batting Structure | South campus | 9030 | Athletics | 7481.2591
11 | Baseball Batting Structure | South campus | 9030 | Athletics | 6627.7274
12 | Baseball Batting Structure | South campus | 9030 | Athletics | 5784.1319
1 | Concession Buildings | South campus | 4320 | Storage | 2159.6552 |  |  |  | 23.7738 | 0 |  |  | 23.7738
2 | Concession Buildings | South campus | 4320 | Storage | 2135.0347
3 | Concession Buildings | South campus | 4320 | Storage | 2743.8467
4 | Concession Buildings | South campus | 4320 | Storage | 2776.9694
5 | Concession Buildings | South campus | 4320 | Storage | 2740.3169
6 | Concession Buildings | South campus | 4320 | Storage | 2492.2637
7 | Concession Buildings | South campus | 4320 | Storage | 3050.1333
8 | Concession Buildings | South campus | 4320 | Storage | 3369.7564
9 | Concession Buildings | South campus | 4320 | Storage | 2740.4992
10 | Concession Buildings | South campus | 4320 | Storage | 2315.9502
11 | Concession Buildings | South campus | 4320 | Storage | 2061.9075
12 | Concession Buildings | South campus | 4320 | Storage | 1514.1788
1 | Modular Building A | South campus | 1440 | Office | 982.1486 |  |  |  | 32.1138 | 0 |  |  | 32.1138
2 | Modular Building A | South campus | 1440 | Office | 945.4361
3 | Modular Building A | South campus | 1440 | Office | 984.0779
4 | Modular Building A | South campus | 1440 | Office | 946.0426
5 | Modular Building A | South campus | 1440 | Office | 949.2398
6 | Modular Building A | South campus | 1440 | Office | 1026.5668
7 | Modular Building A | South campus | 1440 | Office | 1065.3226
8 | Modular Building A | South campus | 1440 | Office | 1541.0204
9 | Modular Building A | South campus | 1440 | Office | 1490.9718
10 | Modular Building A | South campus | 1440 | Office | 1406.3758
11 | Modular Building A | South campus | 1440 | Office | 1200.1229
12 | Modular Building A | South campus | 1440 | Office | 1015.986
1 | Modular Building B | South campus | 1440 | Office | 982.1486 |  |  |  | 32.1138 | 0 |  |  | 32.1138
2 | Modular Building B | South campus | 1440 | Office | 945.4361
3 | Modular Building B | South campus | 1440 | Office | 984.0779
4 | Modular Building B | South campus | 1440 | Office | 946.0426
5 | Modular Building B | South campus | 1440 | Office | 949.2398
6 | Modular Building B | South campus | 1440 | Office | 1026.5668
7 | Modular Building B | South campus | 1440 | Office | 1065.3226
8 | Modular Building B | South campus | 1440 | Office | 1541.0204
9 | Modular Building B | South campus | 1440 | Office | 1490.9718
10 | Modular Building B | South campus | 1440 | Office | 1406.3758
11 | Modular Building B | South campus | 1440 | Office | 1200.1229
12 | Modular Building B | South campus | 1440 | Office | 1015.986
1 | Modular Building C | South campus | 1440 | Office | 982.1486 |  |  |  | 32.1138 | 0 |  |  | 32.1138
2 | Modular Building C | South campus | 1440 | Office | 945.4361
3 | Modular Building C | South campus | 1440 | Office | 984.0779
4 | Modular Building C | South campus | 1440 | Office | 946.0426
5 | Modular Building C | South campus | 1440 | Office | 949.2398
6 | Modular Building C | South campus | 1440 | Office | 1026.5668
7 | Modular Building C | South campus | 1440 | Office | 1065.3226
8 | Modular Building C | South campus | 1440 | Office | 1541.0204
9 | Modular Building C | South campus | 1440 | Office | 1490.9718
10 | Modular Building C | South campus | 1440 | Office | 1406.3758
11 | Modular Building C | South campus | 1440 | Office | 1200.1229
12 | Modular Building C | South campus | 1440 | Office | 1015.986
1 | President's House | President's House | 4350 | Residential | 1455.1964 | 162.9615 |  |  | 15.0896 | 33.4447 |  |  | 48.5343
2 | President's House | President's House | 4350 | Residential | 1477.823 | 178.4814
3 | President's House | President's House | 4350 | Residential | 1661.5331 | 165.6776
4 | President's House | President's House | 4350 | Residential | 1654.8083 | 129.504
5 | President's House | President's House | 4350 | Residential | 1612.4311 | 106.5177
6 | President's House | President's House | 4350 | Residential | 1485.5445 | 81.0258
7 | President's House | President's House | 4350 | Residential | 1597.217 | 68.8091
8 | President's House | President's House | 4350 | Residential | 1797.2905 | 70.2078
9 | President's House | President's House | 4350 | Residential | 1805.4369 | 97.4111
10 | President's House | President's House | 4350 | Residential | 1774.506 | 113.8711
11 | President's House | President's House | 4350 | Residential | 1560.2174 | 136.0583
12 | President's House | President's House | 4350 | Residential | 1355.9426 | 144.3194
1 | Softball & Tennis Facility | South campus | 6540 | Office | 4460.5916 |  |  |  | 32.1138 | 0 |  |  | 32.1138
2 | Softball & Tennis Facility | South campus | 6540 | Office | 4293.8557
3 | Softball & Tennis Facility | South campus | 6540 | Office | 4469.3538
4 | Softball & Tennis Facility | South campus | 6540 | Office | 4296.61
5 | Softball & Tennis Facility | South campus | 6540 | Office | 4311.1308
6 | Softball & Tennis Facility | South campus | 6540 | Office | 4662.3243
7 | Softball & Tennis Facility | South campus | 6540 | Office | 4838.3401
8 | Softball & Tennis Facility | South campus | 6540 | Office | 6998.8008
9 | Softball & Tennis Facility | South campus | 6540 | Office | 6771.4969
10 | Softball & Tennis Facility | South campus | 6540 | Office | 6387.2901
11 | Softball & Tennis Facility | South campus | 6540 | Office | 5450.5584
12 | Softball & Tennis Facility | South campus | 6540 | Office | 4614.2698
1 | South Campus Parking Structure | South campus | 639282 | Parking | 32986.1653 |  |  |  | 2.3067 |  |  |  | 2.3067
2 | South Campus Parking Structure | South campus | 639282 | Parking | 32365.0803
3 | South Campus Parking Structure | South campus | 639282 | Parking | 34571.465
4 | South Campus Parking Structure | South campus | 639282 | Parking | 33957.4556
5 | South Campus Parking Structure | South campus | 639282 | Parking | 35108.6292
6 | South Campus Parking Structure | South campus | 639282 | Parking | 33830.0198
7 | South Campus Parking Structure | South campus | 639282 | Parking | 38086.4499
8 | South Campus Parking Structure | South campus | 639282 | Parking | 38220.311
9 | South Campus Parking Structure | South campus | 639282 | Parking | 37888.0405
10 | South Campus Parking Structure | South campus | 639282 | Parking | 38318.5667
11 | South Campus Parking Structure | South campus | 639282 | Parking | 37292.2787
12 | South Campus Parking Structure | South campus | 639282 | Parking | 39564.734
1 | Spartan Athletic Center | South campus | 55234 | Office | 37672.2197 |  |  |  | 32.1138 | 0 |  |  | 32.1138
2 | Spartan Athletic Center | South campus | 55234 | Office | 36264.0402
3 | Spartan Athletic Center | South campus | 55234 | Office | 37746.221
4 | Spartan Athletic Center | South campus | 55234 | Office | 36287.302
5 | Spartan Athletic Center | South campus | 55234 | Office | 36409.9384
6 | Spartan Athletic Center | South campus | 55234 | Office | 39375.9662
7 | Spartan Athletic Center | South campus | 55234 | Office | 40862.5195
8 | Spartan Athletic Center | South campus | 55234 | Office | 59108.832
9 | Spartan Athletic Center | South campus | 55234 | Office | 57189.122
10 | Spartan Athletic Center | South campus | 55234 | Office | 53944.2786
11 | Spartan Athletic Center | South campus | 55234 | Office | 46033.0491
12 | Spartan Athletic Center | South campus | 55234 | Office | 38970.1193
1 | Training/Locker Facility | South campus | 2684 | Athletics | 1495.4482 |  |  |  | 26.9413 | 0 |  |  | 26.9413
2 | Training/Locker Facility | South campus | 2684 | Athletics | 1444.7999
3 | Training/Locker Facility | South campus | 2684 | Athletics | 1614.5403
4 | Training/Locker Facility | South campus | 2684 | Athletics | 1471.8813
5 | Training/Locker Facility | South campus | 2684 | Athletics | 1490.0781
6 | Training/Locker Facility | South campus | 2684 | Athletics | 1611.4629
7 | Training/Locker Facility | South campus | 2684 | Athletics | 1672.3002
8 | Training/Locker Facility | South campus | 2684 | Athletics | 2240.0722
9 | Training/Locker Facility | South campus | 2684 | Athletics | 2239.5097
10 | Training/Locker Facility | South campus | 2684 | Athletics | 2223.6655
11 | Training/Locker Facility | South campus | 2684 | Athletics | 1969.969
12 | Training/Locker Facility | South campus | 2684 | Athletics | 1719.2259
Note on D27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Plus corp trades area
Note on E51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to theatre only to match EUI as there was Eui for auditorium
Note on E63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to theatre only to match EUI as there was Eui for auditorium
Note on E75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to theatre only to match EUI as there was Eui for auditorium

## Solar Data-Main Campus
kWh | Art | Boccardo Business Classroom | Clark Hall | MLK Library | Music | Sweeney Hall | SPX | SRAC | Student Wellness Center | Yoshihiro Uchida Hall | Total solar | kWh | SRAC Usage | SRAC Solar Total | SRAC Solar Export
1 | 3784 | 8489 | 7937 | 4259 | 7595 | 7527 | 18320 | 30863 | 2602 | 3525 | 94901 | 1 | 125677 | 30863 | 3015
2 | 4795 | 10774 | 10206 | 5008 | 9829 | 9513 | 23487 | 38625 | 3300 | 4663 | 120200 | 2 | 122759 | 38625 | 4193
3 | 6553 | 14396 | 14003 | 6268 | 13460 | 12770 | 32264 | 50953 | 4405 | 6524 | 161596 | 3 | 131618 | 50953 | 9496
4 | 10033 | 21935 | 21345 | 9369 | 20801 | 19396 | 49536 | 78263 | 6667 | 10011 | 247356 | 4 | 122816 | 78263 | 23034
5 | 9766 | 21269 | 21041 | 9286 | 20437 | 19029 | 48347 | 76591 | 6756 | 9739 | 242261 | 5 | 128796 | 76591 | 19653
6 | 10681 | 23528 | 23032 | 9944 | 22435 | 20961 | 53208 | 83782 | 7247 | 10556 | 265374 | 6 | 119102 | 83782 | 25332
7 | 11794 | 26164 | 25068 | 10537 | 23768 | 23045 | 58566 | 90448 | 7740 | 11602 | 288732 | 7 | 122728 | 90448 | 29071
8 | 10104 | 23053 | 21655 | 9360 | 19850 | 20003 | 49197 | 76547 | 6655 | 9995 | 246419 | 8 | 127633 | 76547 | 19758
9 | 7590 | 17340 | 16133 | 7575 | 14464 | 14909 | 35049 | 56317 | 5122 | 7450 | 181949 | 9 | 119934 | 56317 | 9672
10 | 6801 | 15290 | 14091 | 6946 | 12364 | 13269 | 30451 | 49625 | 4661 | 6557 | 160055 | 10 | 127769 | 49625 | 6825
11 | 4627 | 10363 | 9417 | 5168 | 8323 | 9065 | 20466 | 34271 | 3215 | 4243 | 109158 | 11 | 117497 | 34271 | 3731
12 | 3127 | 7076 | 6415 | 3624 | 5668 | 6246 | 14166 | 23935 | 2159 | 2848 | 75264 | 12 | 119289 | 23935 | 887
Total kWh | 89655 | 199676 | 190343 | 87347 | 178994 | 175733 | 433058 | 690221 | 60529 | 87712
DC kW | 58 | 117 | 131 | 58 | 80 | 102 | 583 | 445 | 73 | 401
AC kW | 50 | 100 | 100 | 50 | 60 | 86 | 480 | 372 | 60 | 316
kWh/kW DC | 1538 | 1712 | 1451 | 1498 | 2232 | 1722 | 743 | 1552 | 830 | 219
kWh/kW AC | 1793 | 1997 | 1903 | 1747 | 2983 | 2043 | 902 | 1855 | 1009 | 278
SkySpark Data
1 | 98751.931 | 95210.569 | 64169.938 | 347888.5657 | 15674.1034 | 27602.2586 | 43042.75 | 88851.5909 | 16215.2955 | 28571.1638
2 | 96352 | 85962.5 | 32673.156 | 331966.6406 | 14052 | 26236 | 53340 | 74720.75 | 14668 | 25835.5
3 | 101252.3015 | 91537.4121 | 32673.156 | 350311.6211 | 13510.201 | 23054.1346 | 54715.875 | 64608.1239 | 14941.9554 | 27316.0521
4 | 94623.6985 | 86044.5879 | 57110.375 | 330053.1406 | 9574.799 | 16784.3654 | 52914.75 | 35142.1261 | 12311.1696 | 23452.1979
5 | 94567 | 94838 | 0 | 336548.1406 | 9148.5 | 16474.5 | 49630 | 38198.5 | 13012.125 | 22303.5
6 | 66203.5714 | 96736.4634 | 37692.101 | 314950.4015 | 6513.1098 | 11786.5714 | 48220.75 | 22262.3571 | 10883.5976 | 19456.0714
7 | 58777.4286 | 94350.5366 | 64780.156 | 331711.5282 | 7158.8902 | 10331.9286 | 47051 | 22687.1429 | 11242.5572 | 20295.4286
8 | 45631.5571 | 91171 | 51937.625 | 316330.0893 | 9543.35 | 13404.8429 | 50924 | 43866.55 | 13090.9776 | 24113.35
9 | 49508.5143 | 96784.963 | 67725.313 | 304127.0913 | 11769.0607 | 21855.05 | 52806 | 51883.325 | 14713.4837 | 26067.2333
10 | 55579.4286 | 96859.037 | 68362.437 | 308616.7491 | 14087.3393 | 27285.1071 | 58148 | 70783.625 | 16622.7589 | 29862.6667
11 | 52589.3581 | 89570.8392 | 55756 | 287355.337 | 17368.7809 | 28718.6211 | 53666 | 76702.3985 | 16182.0404 | 30724.3285
12 | 45972.3315 | 89067.6263 | 59291.75 | 303753.6107 | 16423.8484 | 28482.0858 | 42197.2809 | 87867.5325 | 17346.593 | 33103.9646
SkySpark Data+Solar
| Art | Boccardo Business Classroom | Clark Hall | MLK Library | Music | Sweeney Hall | SPX | SRAC | Student Wellness Center | Yoshihiro Uchida Hall
1 | 102535.931 | 103699.569 | 72106.938 | 352147.5657 | 23269.1034 | 35129.2586 | 61362.75 | 119714.5909 | 18817.2955 | 32096.1638
2 | 101147 | 96736.5 | 42879.156 | 336974.6406 | 23881 | 35749 | 76827 | 113345.75 | 17968 | 30498.5
3 | 107805.3015 | 105933.4121 | 46676.156 | 356579.6211 | 26970.201 | 35824.1346 | 86979.875 | 115561.1239 | 19346.9554 | 33840.0521
4 | 104656.6985 | 107979.5879 | 78455.375 | 339422.1406 | 30375.799 | 36180.3654 | 102450.75 | 113405.1261 | 18978.1696 | 33463.1979
5 | 104333 | 116107 | 21041 | 345834.1406 | 29585.5 | 35503.5 | 97977 | 114789.5 | 19768.125 | 32042.5
6 | 76884.5714 | 120264.4634 | 60724.101 | 324894.4015 | 28948.1098 | 32747.5714 | 101428.75 | 106044.3571 | 18130.5976 | 30012.0714
7 | 70571.4286 | 120514.5366 | 89848.156 | 342248.5282 | 30926.8902 | 33376.9286 | 105617 | 113135.1429 | 18982.5572 | 31897.4286
8 | 55735.5571 | 114224 | 73592.625 | 325690.0893 | 29393.35 | 33407.8429 | 100121 | 120413.55 | 19745.9776 | 34108.35
9 | 57098.5143 | 114124.963 | 83858.313 | 311702.0913 | 26233.0607 | 36764.05 | 87855 | 108200.325 | 19835.4837 | 33517.2333
10 | 62380.4286 | 112149.037 | 82453.437 | 315562.7491 | 26451.3393 | 40554.1071 | 88599 | 120408.625 | 21283.7589 | 36419.6667
11 | 57216.3581 | 99933.8392 | 65173 | 292523.337 | 25691.7809 | 37783.6211 | 74132 | 110973.3985 | 19397.0404 | 34967.3285
12 | 49099.3315 | 96143.6263 | 65706.75 | 307377.6107 | 22091.8484 | 34728.0858 | 56363.2809 | 111802.5325 | 19505.593 | 35951.9646

## Split meters
[5 empty] | Split energy |  |  |  | Benchmark Energy |  |  |  | Benchmark % of total |  |  |  | EUI(kBtu/sq.ft)
Month | Building Name | Campus Center | Area | Building Use Type | Electricity 1 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Electricity 1 (kBtu) | Gas (kBtu) | Steam (kBtu) | Chilled Water (kBtu) | Electricity 1 | Gas | Steam | Chilled Water | Electric EUI | Steam EUI | CHW EUI | Total EUI | Electricity 1 (kWh)
1 | Campus Village 1 | Main campus | 960662 | Residential | 365132.591 |  |  |  | 17963614.2654 |  |  |  | 0.96498 |  |  |  | 15.7982 |  |  |  | 378384.7809
2 | Campus Village 1 | Main campus | 960662 | Residential | 356083.4512 | [15 empty] | 369007.21
3 | Campus Village 1 | Main campus | 960662 | Residential | 377928.5929 | [15 empty] | 391645.2033
4 | Campus Village 1 | Main campus | 960662 | Residential | 409551.7882 | [15 empty] | 424416.1367
5 | Campus Village 1 | Main campus | 960662 | Residential | 402231.0613 | [15 empty] | 416829.71
6 | Campus Village 1 | Main campus | 960662 | Residential | 218147.318 | [15 empty] | 226064.7971
7 | Campus Village 1 | Main campus | 960662 | Residential | 319954.1863 | [15 empty] | 331566.6629
8 | Campus Village 1 | Main campus | 960662 | Residential | 358366.5288 | [15 empty] | 371373.15
9 | Campus Village 1 | Main campus | 960662 | Residential | 416098.2529 | [15 empty] | 431200.2
10 | Campus Village 1 | Main campus | 960662 | Residential | 439122.0046 | [15 empty] | 455059.58
11 | Campus Village 1 | Main campus | 960662 | Residential | 403710.4624 | [15 empty] | 418362.8048
12 | Campus Village 1 | Main campus | 960662 | Residential | 381723.4807 | [15 empty] | 395577.8235
1 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 13252.1899 |  |  |  | 651974.7457 |  |  |  | 0.035023 |  |  |  | 1.8944
2 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 12923.7588
3 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 13716.6104
4 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 14864.3485
5 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 14598.6487
6 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 7917.4792
7 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 11612.4765
8 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 13006.6212
9 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 15101.9471
10 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 15937.5754
11 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 14652.3424
12 | CAMPUS VILLAGE GARAGE | Main campus | 290760 | Parking | 13854.3428
1
South Campus Solar Meter | [20 empty] | Month | SJSU South Campus Solar Duke Energy PPA(kWh) | Total Elec without Solar(absolute) | Total Elec without Solar | Total(solar+elec) | SkySpark data | SkySpark data(absolute) | % of total | Total(SkySpark+split solar)
1 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [12 empty] | 165.4498 |  |  |  | 1 | 38393 | 71999.8944 | 71999.8944 | 110392.8944 | 17200.0611 | 17200.0611 |  | 33373.0514
2 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 2 | 47917 | 68902.6243 | 68902.6243 | 116819.6243 | 38549.1243 | 38549.1243 |  | 58734.0845
3 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 3 | 65898 | 43459.7302 | 43459.7302 | 109357.7302 | 24508.8129 | 24508.8129 |  | 52268.2408
4 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 4 | 100621 | 7950.1675 | 6339.7435 | 106960.7435 | 6790.317 | 6790.317 |  | 49176.7535
5 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 5 | 102870 | 38370.1996 | 1125.4504 | 103995.4504 | -2175.1091 | 2175.1091 |  | 43333.8242
6 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 6 | 111250 | 26251.7583 | -23455.1583 | 87794.8417 | -3924.3857 | 3924.3857 |  | 46863.8859
7 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 7 | 115450 | 19834.8584 | -19834.8584 | 95615.1416 | -8.2277 | 8.2277 |  | 48633.1293
8 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 8 | 92078 | 48221.9047 | 48221.9047 | 140299.9047 | 17968.5047 | 17968.5047 |  | 56756.2161
9 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 9 | 64183 | 62997.531 | 62997.531 | 127180.531 | 21630.431 | 21630.431 |  | 48667.4179
10 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 10 | 61039 | 63112.7048 | 63112.7048 | 124151.7048 | 22556.4516 | 22556.4516 |  | 48269.0335
11 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 11 | 42635 | 62444.8363 | 62444.8363 | 105079.8363 | 23440.396 | 23440.396 |  | 41400.3221
12 | CEFCU Stadium | South campus | 11541 | Outdoor Athletics | [16 empty] | 12 | 31066 | 55288.9084 | 55288.9084 | 86354.9084 | 19067.0697 | 19067.0697 | 0.42125 | 32153.5729
1 | Field House | South campus | 15667 | Athletics | [12 empty] | 27.0704 | [8 empty] | 5483.2312 | 5483.2312 |  | 8729.5697
2 | Field House | South campus | 15667 | Athletics | [21 empty] | 4382.2688 | 4382.2688 |  | 8433.9138
3 | Field House | South campus | 15667 | Athletics | [21 empty] | 3852.7242 | 3852.7242 |  | 9424.7613
4 | Field House | South campus | 15667 | Athletics | [21 empty] | 83.9424 | 83.9424 |  | 8591.9995
5 | Field House | South campus | 15667 | Athletics | [21 empty] | -4073.6 | 4073.6 |  | 8698.2223
6 | Field House | South campus | 15667 | Athletics | [21 empty] | -5268.4909 | 5268.4909 |  | 9406.7972
7 | Field House | South campus | 15667 | Athletics | [21 empty] | -3851.6677 | 3851.6677 |  | 9761.9302
8 | Field House | South campus | 15667 | Athletics | [21 empty] | 5290.5586 | 5290.5586 |  | 13076.2582
9 | Field House | South campus | 15667 | Athletics | [21 empty] | 7645.95 | 7645.95 |  | 13072.9744
10 | Field House | South campus | 15667 | Athletics | [21 empty] | 7819.3031 | 7819.3031 |  | 12980.4851
11 | Field House | South campus | 15667 | Athletics | [21 empty] | 7894.5276 | 7894.5276 |  | 11499.5505
12 | Field House | South campus | 15667 | Athletics | [21 empty] | 7996.6774 | 7996.6774 | 0.084555 | 10623.478
1 | Koret Center | South campus | 15358 | Athletics | [12 empty] | 47.2726 | [8 empty] | 30129.5269 | 30129.5269 |  | 36004.6701
2 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 10035.5731 | 10035.5731 |  | 17368.14
3 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 3033.2405 | 3033.2405 |  | 13117.3754
4 | Koret Center | South campus | 15358 | Athletics | [21 empty] | -26.1322 | 26.1322 |  | 15397.6712
5 | Koret Center | South campus | 15358 | Athletics | [21 empty] | -3499.675 | 3499.675 |  | 15741.8276
6 | Koret Center | South campus | 15358 | Athletics | [21 empty] | -4610.4727 | 4610.4727 |  | 17024.1889
7 | Koret Center | South campus | 15358 | Athletics | [21 empty] | -3568.7273 | 3568.7273 |  | 17666.8999
8 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 6998 | 6998 |  | 21088.3665
9 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 9178 | 9178 |  | 18999.6946
10 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 8254.2023 | 8254.2023 |  | 17594.7818
11 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 6416.4106 | 6416.4106 |  | 12940.6919
12 | Koret Center | South campus | 15358 | Athletics | [21 empty] | 5084 | 5084 | 0.15303 | 9837.9187
1 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [12 empty] | 5.8904 | [8 empty] | 6418.8333 | 6418.8333 |  | 12520.8724
2 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 5902.8333 | 5902.8333 |  | 13518.5811
3 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 4736.9868 | 4736.9868 |  | 15210.5671
4 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | -350.9451 | 350.9451 |  | 15992.3233
5 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 19747.825 | 19747.825 |  | 36097.5959
6 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 1398.3 | 1398.3 |  | 19079.9566
7 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | -4273.8966 | 4273.8966 |  | 18349.1888
8 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 5085.6966 | 5085.6966 |  | 19720.2276
9 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 7363.45 | 7363.45 |  | 17564.4547
10 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 7900.948 | 7900.948 |  | 17602.2571
11 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 8262.5439 | 8262.5439 |  | 15038.7905
12 | Outdoor Physical Education | South Campus | 123650 | Outdoor Athletics | [21 empty] | 7835.2581 | 7835.2581 | 0.15894 | 12772.7713
1 | Simpkins Athletics Building | South campus | 22495 | Athletics | [12 empty] | 8.9424 | [8 empty] | 3086.7957 | 3086.7957 |  | 4620.5946
2 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 2272.571 | 2272.571 |  | 4186.8533
3 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 1530.2784 | 1530.2784 |  | 4162.9011
4 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | -428.1347 | 428.1347 |  | 4019.8052
5 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | -2094.6438 | 2094.6438 |  | 4109.6527
6 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | -2325.0182 | 2325.0182 |  | 4444.4334
7 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | -1613.906 | 1613.906 |  | 4612.2232
8 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 2218.7241 | 2218.7241 |  | 5897.2368
9 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 3322 | 3322 |  | 5886.1085
10 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 3581.1793 | 3581.1793 |  | 6019.6851
11 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 3992.0465 | 3992.0465 |  | 5695.3131
12 | Simpkins Athletics Building | South campus | 22495 | Athletics | [21 empty] | 4060.1935 | 4060.1935 | 0.03995 | 5301.2791
1 | Simpkins Stadium Center | South campus | 22203 | Office | [12 empty] | 32.1152 | [8 empty] | 9681.4462 | 9681.4462 |  | 15144.1361
2 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 7760.2538 | 7760.2538 |  | 14578.0516
3 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 5797.6873 | 5797.6873 |  | 15173.8845
4 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 270.696 | 270.696 |  | 14587.4027
5 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | -6779.3468 | 6779.3468 |  | 14636.7023
6 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | -8725.0907 | 8725.0907 |  | 15829.0379
7 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | -6518.4332 | 6518.4332 |  | 16426.6285
8 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 10660.4207 | 10660.4207 |  | 23761.5996
9 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 13857.7 | 13857.7 |  | 22989.881
10 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 13000.6205 | 13000.6205 |  | 21685.4622
11 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 12438.9117 | 12438.9117 |  | 18505.1682
12 | Simpkins Stadium Center | South campus | 22203 | Office | [21 empty] | 11245.7097 | 11245.7097 | 0.14228 | 15665.8885

## Median Monthly EUIs
Main Campus: Median Monthly EUI(kBtu/sq.ft) | [5 empty] | Off Campus: Median Monthly EUI(kBtu/sq.ft) |  | Count |  |  |  | Steam-full campus average ( not needed)
Month | Program | Electricity | Gas | Steam | CHW | Electricity | Gas | Electricity | Gas | Steam | CHW | Area | Usage(Therms) | Average EUI(kBtu/sq.ft)
1 | Academic | 1.9324 | 0.038034 | 4.4745 | 0.41583 | 0.48695 | 0.77573 | 13 |  |  |  | 1129862 | 50735.3276 | 4.4904
2 | Academic | 1.9346 | 0.06325 | 3.1112 | 0.43833 | 0.58471 | 0.9559 |  |  |  |  | 1129862 | 38348.622 | 3.3941
3 | Academic | 2.233 | 0.072068 | 4.2298 | 0.22574 | 0.57 | 0.98201 |  |  |  |  | 1129862 | 46590.2218 | 4.1235
4 | Academic | 2.124 | 0.081139 | 2.8681 | 0.76847 | 0.66997 | 0.72111 |  |  |  |  | 1129862 | 34610.3168 | 3.0632
5 | Academic | 2.064 | 0.068872 | 2.3876 | 0.97733 | 0.71783 | 0.38359 |  |  |  |  | 1129862 | 25718.5016 | 2.2763
6 | Academic | 1.982 | 0.059325 | 1.0777 | 1.644 | 0.79184 | 0.21144 |  |  |  |  | 1129862 | 14306.4601 | 1.2662
7 | Academic | 2.0636 | 0.062743 | 0.89773 | 1.9634 | 0.65544 | 0.099346 |  |  |  |  | 1129862 | 15748.4582 | 1.3938
8 | Academic | 2.1495 | 0.063038 | 0.40485 | 3.3681 | 0.8597 | 0.241 |  |  |  |  | 1129862 | 9225.8838 | 0.81655
9 | Academic | 2.4219 | 0.081856 | 0.75581 | 2.5378 | 0.89043 | 0.44069 |  |  |  |  | 1129862 | 10301.4588 | 0.91174
10 | Academic | 2.5766 | 0.080855 | 1.9071 | 2.554 | 0.67133 | 0.23833 |  |  |  |  | 1129862 | 23594.3889 | 2.0883
11 | Academic | 2.3754 | 0.072159 | 3.7099 | 0.93839 | 0.57745 | 0.30309 |  |  |  |  | 1129862 | 41281.9113 | 3.6537
12 | Academic | 2.384 | 0.065219 | 3.239 | 0.72034 | 0.50553 | 0.5004 |  |  |  |  | 1129862 | 48360.9404 | 4.2803
1 | Office | 2.3333 | 1.3881 | 4.3146 | 0.43368 | 2.3272 | 6.1842
2 | Office | 2.2164 | 1.6613 | 4.1986 | 0.34486 | 2.2403 | 6.2302
3 | Office | 2.3344 | 1.3571 | 3.6509 | 0.60339 | 2.3318 | 6.4114
4 | Office | 2.3193 | 0.73563 | 2.2379 | 0.79635 | 2.2417 | 5.1592
5 | Office | 2.2123 | 0.47978 | 1.6674 | 0.92557 | 2.2493 | 3.2398
6 | Office | 2.1333 | 0.21621 | 1.0441 | 0.86909 | 2.4325 | 2.4
7 | Office | 2.2052 | 0.59428 | 1.0615 | 0.98459 | 2.5243 | 2.5768
8 | Office | 2.3515 | 0.73055 | 0.82026 | 1.0185 | 3.6515 | 2.5462
9 | Office | 2.2189 | 0.47136 | 0.97433 | 0.89352 | 3.5329 | 2.6318
10 | Office | 2.2005 | 0.33933 | 1.4296 | 0.89225 | 3.3325 | 4.0591
11 | Office | 2.1321 | 0.61058 | 2.5751 | 0.67126 | 2.8437 | 5.2429
12 | Office | 2.3014 | 1.3172 | 3.7124 | 0.51809 | 2.4074 | 5.1669
1 | Residential | 1.3012 | 3.2813 | 5.1548 | 0.29376 | 1.1415 | 3.7462
2 | Residential | 1.7098 | 4.9097 | 5.1672 | 0.50827 | 1.1592 | 4.103
3 | Residential | 1.7685 | 4.0513 | 4.7194 | 0.65826 | 1.3033 | 3.8087
4 | Residential | 1.6637 | 2.5443 | 3.7822 | 0.89468 | 1.298 | 2.9771
5 | Residential | 1.5329 | 2.2824 | 1.6885 | 1.0869 | 1.2648 | 2.4487
6 | Residential | 1.0348 | 1.0788 | 0.971 | 1.1283 | 1.1653 | 1.8627
7 | Residential | 1.1802 | 1.159 | 0.71553 | 1.7333 | 1.2529 | 1.5818
8 | Residential | 1.6245 | 1.1715 | 0.47862 | 2.2064 | 1.4098 | 1.614
9 | Residential | 1.9489 | 1.6908 | 1.5297 | 1.744 | 1.4162 | 2.2393
10 | Residential | 1.9539 | 2.478 | 2.2094 | 1.6463 | 1.3919 | 2.6177
11 | Residential | 1.6849 | 3.1984 | 3.2987 | 0.77412 | 1.2238 | 3.1278
12 | Residential | 1.3948 | 3.8008 | 4.2599 | 0.48582 | 1.0636 | 3.3177
1 | Library | 3.1336 | #VALUE! | 2.5493 | 1.502 | #VALUE! | #VALUE!
2 | Library | 2.4937 | #VALUE! | 2.415 | 1.4321 | #VALUE! | #VALUE!
3 | Library | 2.4942 | #VALUE! | 2.1925 | 1.634 | #VALUE! | #VALUE!
4 | Library | 2.407 | #VALUE! | 1.1343 | 2.1062 | #VALUE! | #VALUE!
5 | Library | 2.4674 | #VALUE! | 0.84603 | 2.3925 | #VALUE! | #VALUE!
6 | Library | 2.0079 | #VALUE! | 0.43078 | 2.7636 | #VALUE! | #VALUE!
7 | Library | 2.1028 | #VALUE! | 0.25781 | 3.5262 | #VALUE! | #VALUE!
8 | Library | 1.9448 | #VALUE! | 0.17915 | 3.7813 | #VALUE! | #VALUE!
9 | Library | 2.2167 | #VALUE! | 0.2974 | 3.2838 | #VALUE! | #VALUE!
10 | Library | 2.3751 | #VALUE! | 0.45885 | 3.0006 | #VALUE! | #VALUE!
11 | Library | 2.4822 | #VALUE! | 1.118 | 2.0031 | #VALUE! | #VALUE!
12 | Library | 2.484 | #VALUE! | 1.7888 | 1.8485 | #VALUE! | #VALUE!
1 | Lab | 2.4994 | 0.3388 | 8.3303 | 1.1726 | 3.8917 | 7.7302
2 | Lab | 2.4927 | 0.74657 | 7.61 | 1.1516 | 3.7435 | 7.7614
3 | Lab | 3.839 | 0.88263 | 8.2668 | 1.2497 | 4.0871 | 8.0561
4 | Lab | 4.0224 | 0.0041153 | 5.9416 | 1.8632 | 3.9005 | 6.9718
5 | Lab | 4.167 | 0.54384 | 4.1971 | 2.2791 | 3.8877 | 5.3081
6 | Lab | 3.0711 | 0.1096 | 3.3249 | 2.0145 | 3.7914 | 3.4852
7 | Lab | 2.8189 | 0.10228 | 2.9286 | 2.8009 | 3.897 | 3.0648
8 | Lab | 2.2263 | 0.0070533 | 2.5676 | 3.2943 | 3.9371 | 2.7739
9 | Lab | 2.3474 | 0.53791 | 3.1367 | 2.4996 | 3.8627 | 1.9651
10 | Lab | 2.5813 | 0.0072726 | 4.0756 | 2.9316 | 4.0146 | 3.2843
11 | Lab | 2.6502 | 0.0025286 | 3.0799 | 1.6491 | 3.9225 | 6.4525
12 | Lab | 2.7716 | 0.024959 | 3.768 | 0.66789 | 3.7581 | 7.1533
1 | Athletics | 2.5884 | #VALUE! | 8.1679 | 0.259 | 1.9011 | 3.7172
2 | Athletics | 2.7273 | #VALUE! | 7.5412 | 0.27722 | 1.8368 | 11.2176
3 | Athletics | 2.9084 | #VALUE! | 7.0825 | 0.29239 | 2.0525 | 8.7058
4 | Athletics | 3.1067 | #VALUE! | 3.6695 | 0.62121 | 1.8712 | 2.2665
5 | Athletics | 3.06 | #VALUE! | 0.4242 | 1.021 | 1.8943 | 0.99848
6 | Athletics | 2.9882 | #VALUE! | 0.13463 | 1.3853 | 2.0486 | 0.45989
7 | Athletics | 3.1496 | #VALUE! | 0.091487 | 2.3135 | 2.126 | 0.38297
8 | Athletics | 3.1707 | #VALUE! | 0.082405 | 3.5201 | 2.8478 | 0.34191
9 | Athletics | 2.8179 | #VALUE! | 0.10675 | 2.0783 | 2.8471 | 0.56048
10 | Athletics | 3.0005 | #VALUE! | 0.13928 | 1.9105 | 2.8269 | 0.41366
11 | Athletics | 2.6542 | #VALUE! | 4.9893 | 0.52567 | 2.5044 | 1.1587
12 | Athletics | 2.4034 | #VALUE! | 7.1031 | 0.3497 | 2.1856 | 1.3856
1 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.7034 | 2.913
2 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.3586 | 3.687
3 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.2293 | 3.1446
4 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.736 | 1.6527
5 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.3916 | 1.1152
6 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.6594 | 1.0282
7 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.2321 | 0.19068
8 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.3927 | 0.067621
9 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.9085 | 0.16927
10 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.2773 | 0.48022
11 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.7208 | 1.4015
12 | Theater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.5337 | 2.6983
1 | Food Service | 7.4662 | 15.5352 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | Food Service | 10.6817 | 19.1145 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | Food Service | 10.5818 | 17.4449 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | Food Service | 12.1945 | 15.347 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | Food Service | 10.5403 | 11.0714 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | Food Service | 7.5761 | 6.5574 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | Food Service | 8.3281 | 5.8248 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | Food Service | 13.1395 | 9.7269 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | Food Service | 15.1326 | 13.3918 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | Food Service | 14.7852 | 14.6805 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | Food Service | 11.9301 | 14.7806 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | Food Service | 7.4706 | 11.9248 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7058 | 6.2809
2 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6864 | 8.6497
3 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1672 | 15.1054
4 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1934 | 4.462
5 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1644 | 1.2652
6 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9685 | 0.32933
7 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4091 | 0.16263
8 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.6616 | 0.064402
9 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1646 | 0.80413
10 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8292 | 1.29
11 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6286 | 5.1904
12 | Storage | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.196 | 3.7354
1 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | Warehouse | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 5.106 | #VALUE!
2 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8.8686 | #VALUE!
3 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.9362 | #VALUE!
4 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.49 | #VALUE!
5 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.9037 | #VALUE!
6 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.1907 | #VALUE!
7 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.4422 | #VALUE!
8 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8.6618 | #VALUE!
9 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.4364 | #VALUE!
10 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.378 | #VALUE!
11 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.3273 | #VALUE!
12 | Outdoor Athletics | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.9292 | #VALUE!
1 | Parking | 0.17606 |  |  |  | 0.17606
2 | Parking | 0.17275 |  |  |  | 0.17275
3 | Parking | 0.18452 |  |  |  | 0.18452
4 | Parking | 0.18125 |  |  |  | 0.18125
5 | Parking | 0.18739 |  |  |  | 0.18739
6 | Parking | 0.18057 |  |  |  | 0.18057
7 | Parking | 0.20328 |  |  |  | 0.20328
8 | Parking | 0.204 |  |  |  | 0.204
9 | Parking | 0.20223 |  |  |  | 0.20223
10 | Parking | 0.20452 |  |  |  | 0.20452
11 | Parking | 0.19905 |  |  |  | 0.19905
12 | Parking | 0.21118 |  |  |  | 0.21118

## Data availability
Facility Name | Campus Center | Data Availability_Electric | Data Availability_Gas | Data Availability_CHW | Data Availability_Steam | Gross Square Feet | Building Use Type
4th Street Building | Off Campus 4th Street | N | N | - | - | 19857 | Office | Type | EUI(Gas) | Data Availability_Gas | Q1 | Q3 | IQR | Lower | Upper | Is Outlier?
Administration | Main campus | Y | - | N | N | 39323 | Office | Storage | 47.3396 | Y | 47.3396 | 47.3396 | 0 | 47.3396 | 47.3396 | FALSE
Art | Main campus | Y | Y | Y | Y | 85419 | Lab | Academic | 0.0061174 | Y | 0.60795 | 4.6724 | 4.0644 | -3.4565 | 8.7368 | FALSE
Art Foundry | Art Foundry | Y | Y | - | - | 7934 | Storage | Outdoor Athletics | 0 | Y | 0 | 0 | 0 | 0 | 0 | FALSE
Associated Students House | Main campus | Y | - | - | - | 8591 | Office | Academic | 0.80856 | Y | 0.60795 | 4.6724 | 4.0644 | -3.4565 | 8.7368 | FALSE
Automated Bank Teller Facility | Main campus | Y | - | - | - | 1396 | Office | Academic | 7.1905 | Y | 0.60795 | 4.6724 | 4.0644 | -3.4565 | 8.7368 | FALSE
Bally Hut | South campus | N | - | - | - | 342 | Infrastructure | Office | 21.7167 | Y | 20.6136 | 38.0457 | 17.4321 | 3.1816 | 55.4777 | FALSE
Baseball Batting Structure | South campus | N | - | - | - | 9030 | Athletics | Food Service | 155.3999 | Y | 155.3999 | 155.3999 | 0 | 155.3999 | 155.3999 | FALSE
Boccardo Business Classroom Building | Main campus | Y | - | Y | Y | 83173 | Academic | Lab | 0.075595 | Y | 3.1772 | 9.3804 | 6.2032 | -3.026 | 15.5835 | FALSE
Business Tower | Main campus | - | - | - | - | 54428 | Office | Athletics | 32.9273 | Y | 13.0677 | 35.5294 | 22.4617 | -9.3941 | 57.9912 | FALSE
Campus Village Phase 2 | Main campus | Y | - | Y | Y | 186318 | Residential | Theater | 18.5483 | Y | 18.5483 | 18.5483 | 0 | 18.5483 | 18.5483 | FALSE
Campus Village A | Main campus | Y | - | Y | Y | 108150 | Residential | Lab | 12.4819 | Y | 3.1772 | 9.3804 | 6.2032 | -3.026 | 15.5835 | FALSE
Campus Village B | Main campus | Y | - | Y | Y | 716675 | Residential | Office | 33.4447 | Y | 20.6136 | 38.0457 | 17.4321 | 3.1816 | 55.4777 | FALSE
Campus Village C | Main campus | Y | - | Y | Y | 135837 | Residential | Residential | 31.6464 | Y | 7.9116 | 23.7348 | 15.8232 | -7.9116 | 39.558 | FALSE
Campus Village Garage | Main campus | Y | - | - | - | 290760 | Parking | Athletics | 43.3358 | Y | 13.0677 | 35.5294 | 22.4617 | -9.3941 | 57.9912 | FALSE
CEFCU Stadium | South campus | Y | - | - | - | 11541 | Outdoor Athletics | Academic | 3.833 | Y | 0.60795 | 4.6724 | 4.0644 | -3.4565 | 8.7368 | FALSE
Central Classroom Building | Main campus | Y | Y | Y | Y | 33407 | Academic | Athletics | 17.2407 | Y | 13.0677 | 35.5294 | 22.4617 | -9.3941 | 57.9912 | FALSE
Central Plant | Main campus | - | - | - | - | 36755 | Infrastructure | Office | 51.8486 | Y | 20.6136 | 38.0457 | 17.4321 | 3.1816 | 55.4777 | FALSE
Child Development Center | Main campus | Y | Y | - | - | 12889 | Academic | Athletics | 0.54854 | Y | 13.0677 | 35.5294 | 22.4617 | -9.3941 | 57.9912 | FALSE
Computer Center | Main campus | N | - | N | - | 12900 | Data Center | Office | 17.3045 | Y | 20.6136 | 38.0457 | 17.4321 | 3.1816 | 55.4777 | FALSE
Concession Buildings | South campus | N | - | - | - | 4320 | Storage | Residential | 0 | Y | 7.9116 | 23.7348 | 15.8232 | -7.9116 | 39.558 | FALSE
Corporation Yard Offices | Main campus | N | Y | - | - | 12837 | Office
Corporation Yard Trades Building | Main campus | - | - | - | - | 29182 | Warehouse
Dining Commons | Main campus | Y | Y | - | - | 23925 | Food Service
Dudley Moorhead Hall | Main campus | Y | - | Y | Y | 58733 | Academic
Duncan Hall | Main campus | Y | Y | Y | Y | 345715 | Lab
Dwight Bentel Hall | Main campus | Y | - | Y | Y | 36691 | Academic
Engineering | Main campus | Y | - | Y | Y | 341415 | Academic
Faculty Office Building | Main campus | N | - | N | N | 16496 | Office
Field House | South campus | Y | Y | - | - | 15667 | Athletics
Gateways |  | - | - | - | - | 0
Hammer Theater | Off Campus 3rd Street | Y | Y | - | - | 52851 | Theater
Health Building | Main campus | Y | - | Y | Y | 42445 | Academic
Hugh Gillis Hall | Main campus | Y | - | Y | N(Bad Data) | 73315 | Academic
Industrial Studies | Main campus | Y | Y | - | Y | 113302 | Lab
Instructional Resource Center | Main campus | - | - | - | - | 18803 | Academic
Interdisciplinary Science Building | Main campus | Y | - | Y | Y | 163476 | Lab
International House | Off Campus 11th St | Y | Y | - | - | 25320 | Residential
Joe West Hall | Main campus | Y | Y | - | - | 130000 | Residential
Koret Center | South campus | Y | Y | - | - | 15358 | Athletics
MacQuarrie Hall | Main campus | Y | - | Y | Y | 107302 | Academic
Dr. Martin Luther King, Jr. Library | Main campus | Y | - | Y | Y | 499221 | Library
Modular Building A | South campus | N | - | - | - | 1440 | Office
Modular A | Main campus | Y | - | - | - | 1518 | Office
Modular Building B | South campus | N | - | - | - | 1440 | Office
Modular B | Main campus | Y | - | - | - | 1525 | Office
Modular Building C | South campus | N | - | - | - | 1440 | Office
Modular F | Main campus | Y | - | - | - | 3408 | Office
Morris Dailey Auditorium | Main campus | N | - | - | N | 8545 | Auditorium
Moss Landing Marine Lab Aquaculture Facility | Moss Landing | Y | Y | - | - | 1561 | Lab
Moss Landing Marine Lab Main Laboratory | Moss Landing | - | - | - | - | 56704 | Lab
Moss Landing Marine Lab Marine Operations | Moss Landing | - | - | - | - | 2797 | Office
Moss Landing Marine Lab Pumphouse | Moss Landing | - | - | - | - | 1376 | Infrastructure
Moss Landing Marine Lab Shop | Moss Landing | - | - | - | - | 3960 | Infrastructure
Music | Main campus | Y | - | Y | Y | 64072 | Academic
North Parking Facility | Main campus | Y | - | - | - | 580783 | Parking
Outdoor Physical Education | South Campus | Y | - | - | - | 123650 | Outdoor Athletics
President's House | President's House | N | N | - | - | 4350 | Residential
Provident Credit Union Event Center | Main campus | Y | - | Y | Y | 110140 | Athletics
Reid Hillview Airport | Reid Hillview Airport | Y | Y | - | - | 8420 | Academic
Clark Hall | Main campus | Y | - | Y | Y | 192428 | Academic
San Antonio Parking Lot |  | Y | - | - | - | 0 | Parking
Science | Main campus | Y | - | - | Y(Will) | 89180 | Academic
Simpkins Athletics Building | South campus | Y | Y | - | - | 22495 | Athletics
Simpkins Center Storage Building | South campus | Y | - | - | - | 768 | Storage
Simpkins Stadium Center | South campus | Y | Y | - | - | 22203 | Office
Site Improvements |  | - | - | - | - | 0
Soccer Field (Natural Turf) |  | - | - | - | - | 0 | Outdoor Athletics
Softball & Tennis Facility | South campus | N | - | - | - | 6540 | Office
South Campus Parking Structure | South campus | N | - | - | - | 639282 | Parking
South Parking Facility | Main campus | Y | - | - | - | 624735 | Parking
Spartan Athletic Center | South campus | N | - | - | - | 55234 | Office
Spartan Memorial | Main campus | N | - | - | - | 2300 | Auditorium
SPX Central | Main campus | Y | - | Y | Y | 86252 | Athletics
SPX East | Main campus | - | - | - | - | 29240 | Athletics
Storage Building | South campus | Y | - | - | - | 3135 | Storage
Spartan Recreation and Aquatic Center | Main campus | Y | - | Y | Y | 121426 | Athletics
Student Services Center | Main campus | Y | Y | - | - | 99853 | Office
Student Union | Main campus | Y | Y | Y | Y | 226256 | Office
Student Wellness Center | Main campus | Y | - | Y | Y | 52700 | Office
Sweeney Hall | Main campus | Y | - | Y | Y | 101932 | Academic
Tennis Complex | South campus | - | - | - | - | 0 | Outdoor Athletics
Tower Hall | Main campus | N | - | - | N | 13096 | Auditorium
Training/Locker Facility | South campus | N | - | - | - | 2684 | Athletics
UPD Building | Main campus | N | - | N | N | 25391 | Office
Utility Lines |  | - | - | - | - | 0
Washburn Hall (Student Residence) | Main campus | Y | Y | - | - | 39332 | Residential
Washington Square Hall | Main campus | Y | - | Y | Y | 71857 | Academic
West Parking Facility | Main campus | Y | - | - | - | 323350 | Parking
Yoshihiro Uchida Hall | Main campus | Y | - | Y | Y | 76871 | Athletics
|  | Y | N(maybe) | N | N
|  | Y | Y | N | N
|  | Y | N | N | N
Missing Buildings
| Sr.No. | Main campus
|  | Electric | Gas | CHW | Steam
| 1 |  |  | Administration | Administration
| 2 | Computer Center |  | Computer Center
| 3 | Corporation Yard Offices
| 4 | Corporation Yard Trades Building
| 5 |  |  |  | Hugh Gillis Hall
| 6 | Faculty Office Building |  | Faculty Office Building | Faculty Office Building
| 7 | Morris Dailey Auditorium |  |  | Morris Dailey Auditorium
| 8 | Spartan Memorial
| 9 | Tower Hall |  |  | Tower Hall
| 10 | UPD Building |  | UPD Building | UPD Building
| Sr.No. | Off campus
| 1 | 4th Street Building | 4th Street Building
| 2 | Bally Hut
| 3 | Baseball Batting Structure
| 4 | Concession Buildings
| 5 | Modular A
| 6 | Modular B
| 7 | Modular Building C
| 8 | President's House | President's House
| 9 | Softball & Tennis Facility
| 10 | South Campus Parking Structure
| 11 | Spartan Athletic Center
| 12 | Training/Locker Facility
Note on A63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does this exist?

## Campus Totals
| Electric(kWh) | Gas(therms) | Steam(therms) | Chilled Water(tons)
Total campus
Timestamp | 000 RR Main Campus - Distribution Electric |  | 000 RR Main Campus - Distribution Steam(therms) | 000 RR Main Campus - Distribution Chilled Water(tons) |  | 000 RR Main Campus - Distribution Steam(mmbtu) | 000 RR Main Campus - Distribution Chilled Water(mmbtu) |  | 000 RR Main Campus - Distribution Electric
2023-01-01T00:00:00-08:00 Los_Angeles | 3051240.55 |  | 219467.527 | 329955.4952 |  | 21946.7527 | 3959.4675 |  | 3045210.55
2023-02-01T00:00:00-08:00 Los_Angeles | 3121439.93 |  | 220628.9559 | 318945.9619 |  | 22062.8956 | 3827.3531 |  | 3113053.93
2023-03-01T00:00:00-08:00 Los_Angeles | 3348314.27 |  | 238528.9448 | 364757.7472 |  | 23852.8945 | 4377.0947 |  | 3329322.27
2023-04-01T00:00:00-07:00 Los_Angeles | 3157831.46 |  | 177533.0498 | 612730.9113 |  | 17753.305 | 7352.7739 |  | 3111763.46
2023-05-01T00:00:00-07:00 Los_Angeles | 3172535.03 |  | 140818.8718 | 723291.2539 |  | 14081.8872 | 8679.4985 |  | 3133229.03
2023-06-01T00:00:00-07:00 Los_Angeles | 2768614.17 |  | 103744.2027 | 788639.9171 |  | 10374.4203 | 9463.6828 |  | 2717950.17
2023-07-01T00:00:00-07:00 Los_Angeles | 2939915.66 |  | 86764.3252 | 1234690.7124 |  | 8676.4325 | 14816.2945 |  | 2881773.66
2023-08-01T00:00:00-07:00 Los_Angeles | 3107715.32 |  | 83472.2061 | 1273257.6604 |  | 8347.2206 | 15279.098 |  | 3068199.32
2023-09-01T00:00:00-07:00 Los_Angeles | 3200533 |  | 92512.5084 | 1107860.662 |  | 9251.2508 | 13294.3333 |  | 3181189
2023-10-01T00:00:00-07:00 Los_Angeles | 3387652.84 |  | 108982.4354 | 1004117.8541 |  | 10898.2435 | 12049.4191 |  | 3374002.84
2023-11-01T00:00:00-07:00 Los_Angeles | 3208631.04 |  | 166307.6768 | 566473.9802 |  | 16630.7677 | 6797.6905 |  | 3201169.04
2023-12-01T00:00:00-08:00 Los_Angeles | 3119410.62 |  | 202234.6096 | 443989.7178 |  | 20223.461 | 5327.8787 |  | 3117636.62
Total | 37583833.89 |  | 1840995.3134 | 8768711.8736
Total buildings
Month | Buildings' Electric Total | Buildings' Gas Total | Buildings' Steam Total | Buildings' Chilled Water Total
1 | 2832058.9191 | 14752.8493 | 219170.7309 | 246425.4372
2 | 2781546.8936 | 19388.6119 | 200999.6248 | 265880.4931 |  | ton | 12000
3 | 3081556.7721 | 18898.2904 | 202198.2814 | 301360.6364 |  | x | 3959467526.3067
4 | 3055096.3128 | 14751.3812 | 150458.9816 | 454644.7236
5 | 2987257.6812 | 10632.1209 | 85592.1095 | 600797.7056 |  | 329955.6272
6 | 2621909.7707 | 5373.7231 | 59608.4794 | 719549.9586
7 | 2890385.5251 | 4780.8851 | 52625.6614 | 1033376.9025
8 | 2971828.0598 | 7160.2317 | 41327.19 | 1293379.7551
9 | 3160729.6007 | 9257.2237 | 63610.0803 | 959473.9745
10 | 3327935.3188 | 11398.3083 | 93623.8137 | 851229.7007 |  | therm | 100 | kbtu
11 | 3111008.9861 | 13456.0369 | 154023.6704 | 420950.5298 |  |  | 1000000
12 | 3049196.1536 | 13145.0592 | 189454.4525 | 328510.9614
Total | 35870509.9936 | 142994.7218 | 1512693.0759 | 7475580.7784
Balance Energy( Total Campus - Total Building)
Month | Electric Balance |  | Steam Balance | Chilled Water Balance
1 | 219181.6309 |  | 296.7961 | 83530.058
2 | 339893.0364 |  | 19629.3311 | 53065.4688
3 | 266757.4979 |  | 36330.6635 | 63397.1108
4 | 102735.1472 |  | 27074.0682 | 158086.1877
5 | 185277.3488 |  | 55226.7622 | 122493.5484
6 | 146704.3993 |  | 44135.7233 | 69089.9585
7 | 49530.1349 |  | 34138.6638 | 201313.8099
8 | 135887.2602 |  | 42145.0162 | -20122.0946
9 | 39803.3993 |  | 28902.4281 | 148386.6875
10 | 59717.5212 |  | 15358.6217 | 152888.1534
11 | 97622.0539 |  | 12284.0063 | 145523.4504
12 | 70214.4664 |  | 12780.1571 | 115478.7565
Total | 1713323.8964 | -142994.7218 | 328302.2375 | 1293131.0952
Steam Leaks
|  |  | -278050.7293 | 602995.11 | unmetered CHW
|  |  | -0.15103 | 690135.9852 | unmetered balance
|  |  |  | 7.8704 | unmetered balance %
|  | unmetered steam | 44737.82
|  | steam leak | 276149.297
|  | Total balance | 320887.117
1527896
29543.851
1557439.851
Timestamp | 000 RR South Campus Electric (One Month in Arrears) | 000 RR Main Campus - Distribution Electric
2019-01-01T00:00:00-08:00 Los_Angeles | 115613.93296703302kWh | 2944087.529999999kWh
2019-02-01T00:00:00-08:00 Los_Angeles | 109321.1384615385kWh | 3189244.7500000014kWh
2019-03-01T00:00:00-08:00 Los_Angeles | 121034.11758241763kWh | 3443157.3900000006kWh
2019-04-01T00:00:00-07:00 Los_Angeles | 107745.31527472532kWh | 3348383.6599999988kWh
2019-05-01T00:00:00-07:00 Los_Angeles | 107810.5378571429kWh | 3289823.240000003kWh
2019-06-01T00:00:00-07:00 Los_Angeles | 109563.92719047616kWh | 2986179.8599999994kWh
2019-07-01T00:00:00-07:00 Los_Angeles | 141095.45133333333kWh | 3082334.460000001kWh
2019-08-01T00:00:00-07:00 Los_Angeles | 157528.70703825133kWh | 3421021kWh
2019-09-01T00:00:00-07:00 Los_Angeles | 143325.275409836kWh | 3475771.96kWh
2019-10-01T00:00:00-07:00 Los_Angeles | 141899.74905915893kWh | 3539266.0300000007kWh
2019-11-01T00:00:00-07:00 Los_Angeles | 135283.177826087kWh | 3290432.8300000024kWh
2019-12-01T00:00:00-08:00 Los_Angeles |  | 3210457.2999999993kWh
Timestamp | 000 RR South Campus Natural Gas (One Month in Arrears)
2018-11-01T00:00:00-07:00 Los_Angeles | 3663.2900000000013therm
2018-12-01T00:00:00-08:00 Los_Angeles | 4550.280000000003therm
2019-01-01T00:00:00-08:00 Los_Angeles | 4528.039999999999therm
2019-02-01T00:00:00-08:00 Los_Angeles | 3904.581therm
2019-03-01T00:00:00-08:00 Los_Angeles | 4245.687666666666therm
2019-04-01T00:00:00-07:00 Los_Angeles | 2191.3744761904745therm
2019-05-01T00:00:00-07:00 Los_Angeles | 1543.9594285714277therm
2019-06-01T00:00:00-07:00 Los_Angeles | 1210.0329458128076therm
2019-07-01T00:00:00-07:00 Los_Angeles | 938.6428698553946therm
2019-08-01T00:00:00-07:00 Los_Angeles | 1079.7291129032255therm
2019-09-01T00:00:00-07:00 Los_Angeles | 1766.2472126436794therm
2019-10-01T00:00:00-07:00 Los_Angeles | 1960.5326436781625therm
2019-11-01T00:00:00-07:00 Los_Angeles | 1960.5326436781625therm
2019-12-01T00:00:00-08:00 Los_Angeles
Note on E3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ask what this represents

## Outliers
[7 empty] | Total EUI | [6 empty] | Electric EUI | [8 empty] | Gas EUI | [8 empty] | Steam EUI | [8 empty] | CHW EUI
| Electricity | Gas | Steam | Chilled Water | SF | Type | EUI | Q1 | Q3 | IQR | Lower | Upper | Is Outlier? | EUI(electric) | Data Availability_Electric | Q1 | Q3 | IQR | Lower | Upper | Is Outlier? | Helper column for median/mean | EUI(Gas) | Data Availability_Gas | Q1 | Q3 | IQR | Lower | Upper | Is Outlier? | Helper column for median/mean | EUI(Steam) | Data Availability_Steam | Q1 | Q3 | IQR | Lower | Upper | Is Outlier? | Helper column for median/mean | EUI(CHW) | Data Availability_CHW | Q1 | Q3 | IQR | Lower | Upper | Is Outlier? | Helper column for median/mean |  | Count
Administration | 613.4801 | 0 | 0 | 0 | 39323 | Office | 0.053231 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 0.053231 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 0 | - | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | N | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | N | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE | Office | 8
Art Foundry | 55284.128 | 3755.9241 | 0 | 0 | 7934 | Storage | 71.1144 | 3.4305 | 58.8408 | 55.4102 | -51.9797 | 114.251 | FALSE | 23.7748 | Y | 14.1744 | 39.2622 | 25.0877 | -10.9133 | 64.3499 | FALSE | FALSE | 47.3396 | Y | 47.3396 | 47.3396 | 0 | 47.3396 | 47.3396 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | Storage | 4
Art | 949464.1207 | 5.2255 | 40371.6258 | 147665.8952 | 85419 | Lab | 105.9395 | 105.9395 | 123.4257 | 17.4862 | 88.4533 | 140.9119 | FALSE | 37.9257 | Y | 29.8651 | 45.1251 | 15.26 | 14.605 | 60.3852 | FALSE | FALSE | 0.0061174 | Y | 0.058226 | 25.3631 | 25.3049 | -25.2466 | 50.668 | FALSE | FALSE | 47.2631 | Y | 36.1203 | 56.2532 | 20.1329 | 15.9874 | 76.3861 | FALSE | FALSE | 20.7447 | Y | 22.2377 | 42.6621 | 20.4244 | 1.8133 | 63.0864 | FALSE | FALSE | Lab | 3
Associated Students House | 38719.2727 | 0 | 0 | 0 | 8591 | Office | 15.3777 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 15.3777 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 0 | - | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | - | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | - | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE | Academic | 14
Automated Bank Teller Facility | 29048.1262 | 0 | 0 | 0 | 1396 | Office | 70.9973 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 70.9973 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 0 | - | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | - | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | - | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE | Food Service | 2
Boccardo Business Classroom Building +Business Tower | 1307810.5345 | 0 | 71673.1735 | 241805.6673 | 137601 | Academic | 105.6041 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 32.4289 | #N/A | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | #N/A | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 52.0877 | #N/A | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 21.0876 | #N/A | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE | Residential | 4
Business Tower-Jazzland Tenant | 6081 | 0 | 0 | 0 | 0 | Food Service | 0 | 71.3067 | 213.92 | 142.6133 | -71.3067 | 356.5333 | FALSE | 0 | #N/A | 129.8267 | 129.8267 | 0 | 129.8267 | 129.8267 | TRUE | TRUE | 0 | #N/A | 155.3999 | 155.3999 | 0 | 155.3999 | 155.3999 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | 3
Campus Village 1 | 4448049.7183 | 0 | 229493 | 832119 | 960662 | Residential | 50.0816 | 50.0816 | 60.2617 | 10.1801 | 39.9014 | 70.4419 | FALSE | 12.1276 | #N/A | 15.0903 | 20.7689 | 5.6787 | 9.4116 | 26.4476 | FALSE | FALSE | 0 | #N/A | 32.5456 | 36.4687 | 3.9232 | 28.6224 | 40.3919 | TRUE | TRUE | 23.889 | #N/A | 28.932 | 39.0181 | 10.086 | 18.846 | 49.1041 | FALSE | FALSE | 10.3943 | #N/A | 11.7772 | 14.543 | 2.7658 | 9.0114 | 17.3088 | FALSE | FALSE | Outdoor Athletics | 2
Campus Village A-Food Tenant | 150899.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | Warehouse | 1
Campus Village Phase 2 | 1134939.7842 | 0 | 82093.6782 | 247273.8952 | 186318 | Residential | 80.7709 | 50.0816 | 60.2617 | 10.1801 | 39.9014 | 70.4419 | TRUE | 20.7839 | Y | 15.0903 | 20.7689 | 5.6787 | 9.4116 | 26.4476 | FALSE | FALSE | 0 | - | 32.5456 | 36.4687 | 3.9232 | 28.6224 | 40.3919 | TRUE | TRUE | 44.0611 | Y | 28.932 | 39.0181 | 10.086 | 18.846 | 49.1041 | FALSE | FALSE | 15.9259 | Y | 11.7772 | 14.543 | 2.7658 | 9.0114 | 17.3088 | FALSE | FALSE | Library | 2
CEFCU Stadium | 559629.5321 | 0 | 0 | 0 | 11541 | Outdoor Athletics | 165.4498 | 45.7803 | 125.5599 | 79.7797 | -33.9994 | 205.3396 | FALSE | 165.4498 | Y | 45.7803 | 125.5599 | 79.7797 | -33.9994 | 205.3396 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | Athletics | 7
Central Classroom Building | 303598.6207 | 270.1155 | 9903.4018 | 116142.439 | 33407 | Academic | 103.1802 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 31.0078 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0.80856 | Y | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | FALSE | FALSE | 29.6447 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 41.7191 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE | Theater | 1
Child Development Center | 38020.2364 | 926.7879 | 0 | 0 | 12889 | Academic | 17.2553 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 10.0648 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 7.1905 | Y | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | FALSE | FALSE | 0 | - | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | TRUE | TRUE | 0 | - | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | TRUE | TRUE | Food Sale
Clark Hall | 782515.007 | 0 | 34145.6657 | 231395.9012 | 192428 | Academic | 46.0497 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 13.875 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 17.7446 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 14.4301 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Concession Buildings | 0 | 0 | 0 | 0 | 4320 | Storage | 0 | 3.4305 | 58.8408 | 55.4102 | -51.9797 | 114.251 | FALSE | 0 | N | 14.1744 | 39.2622 | 25.0877 | -10.9133 | 64.3499 | TRUE | TRUE | 0 | - | 47.3396 | 47.3396 | 0 | 47.3396 | 47.3396 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Corporation Yard Offices+Yard Trades | 0 | 2787.7667 | 0 | 0 | 42019 | Office | 6.6345 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 0 | #N/A | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | TRUE | TRUE | 6.6345 | #N/A | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | FALSE | FALSE | 0 | #N/A | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | #N/A | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE
Corporation Yard Trades Building | 0 | 0 | 0 | 0 | 29182 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Dining Commons | 910347.16 | 37179.4333 | 0 | 0 | 23925 | Food Service | 285.2267 | 71.3067 | 213.92 | 142.6133 | -71.3067 | 356.5333 | FALSE | 129.8267 | Y | 129.8267 | 129.8267 | 0 | 129.8267 | 129.8267 | FALSE | FALSE | 155.3999 | Y | 155.3999 | 155.3999 | 0 | 155.3999 | 155.3999 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Dr. Martin Luther King, Jr. Library | 3950956.9158 | 0 | 68233.285 | 1217847.8328 | 499221 | Library | 69.9453 | 40.1479 | 60.0128 | 19.8649 | 20.2829 | 79.8778 | FALSE | 27.0034 | Y | 27.8064 | 29.4124 | 1.606 | 26.2004 | 31.0184 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 13.668 | Y | 13.668 | 13.668 | 0 | 13.668 | 13.668 | FALSE | FALSE | 29.274 | Y | 29.274 | 29.274 | 0 | 29.274 | 29.274 | FALSE | FALSE
Dr. Martin Luther King, Jr. Library-Tenants | 21767.1446 | 0 | 0 | 0 | 2458 | Library | 30.2154 | 40.1479 | 60.0128 | 19.8649 | 20.2829 | 79.8778 | FALSE | 30.2154 | #N/A | 27.8064 | 29.4124 | 1.606 | 26.2004 | 31.0184 | FALSE | FALSE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 13.668 | 13.668 | 0 | 13.668 | 13.668 | TRUE | TRUE | 0 | #N/A | 29.274 | 29.274 | 0 | 29.274 | 29.274 | TRUE | TRUE
Duncan Hall | 3026028.5073 | 261.3449 | 241151.1099 | 683671.3769 | 345715 | Lab | 123.4257 | 105.9395 | 123.4257 | 17.4862 | 88.4533 | 140.9119 | FALSE | 29.8651 | Y | 29.8651 | 45.1251 | 15.26 | 14.605 | 60.3852 | FALSE | FALSE | 0.075595 | Y | 0.058226 | 25.3631 | 25.3049 | -25.2466 | 50.668 | FALSE | FALSE | 69.7543 | Y | 36.1203 | 56.2532 | 20.1329 | 15.9874 | 76.3861 | FALSE | FALSE | 23.7307 | Y | 22.2377 | 42.6621 | 20.4244 | 1.8133 | 63.0864 | FALSE | FALSE
Dwight Bentel Hall | 204996.9138 | 0 | 14962.9411 | 11980.4037 | 36691 | Academic | 63.7625 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 19.0632 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 40.781 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 3.9183 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Engineering | 3640859.4867 | 0 | 122149.6606 | 1052101.3006 | 341415 | Academic | 109.1422 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 36.3857 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 35.7775 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 36.9791 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Field House | 124299.9401 | 5222.9 | 0 | 0 | 15667 | Athletics | 60.4073 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 27.0704 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 33.337 | Y | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | FALSE | FALSE | 0 | - | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | TRUE | TRUE | 0 | - | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | TRUE | TRUE
Golf Complex | 77492.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Hammer Theater | 1055524.8235 | 9802.9697 | 0 | 0 | 52851 | Theater | 86.6918 | 86.6918 | 86.6918 | 0 | 86.6918 | 86.6918 | FALSE | 68.1435 | Y | 68.1435 | 68.1435 | 0 | 68.1435 | 68.1435 | FALSE | FALSE | 18.5483 | Y | 18.5483 | 18.5483 | 0 | 18.5483 | 18.5483 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Health Building | 353676.2043 | 0 | 15508.4864 | 123075.5863 | 42445 | Academic | 99.7644 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 28.4308 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 36.5378 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 34.7958 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Hugh Gillis Hall | 580831.7408 | 0 | 0 | 99281.436 | 73315 | Academic | 43.2814 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 27.0313 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 0 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | TRUE | TRUE | 16.2501 | N(Bad Data) | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Industrial Studies | 397894.8722 | 14142.2834 | 3050.1581 | 0 | 113302 | Lab | 27.1563 | 105.9395 | 123.4257 | 17.4862 | 88.4533 | 140.9119 | TRUE | 11.9823 | Y | 29.8651 | 45.1251 | 15.26 | 14.605 | 60.3852 | TRUE | TRUE | 12.4819 | Y | 0.058226 | 25.3631 | 25.3049 | -25.2466 | 50.668 | FALSE | FALSE | 2.6921 | - | 36.1203 | 56.2532 | 20.1329 | 15.9874 | 76.3861 | TRUE | TRUE | 0 | Y | 22.2377 | 42.6621 | 20.4244 | 1.8133 | 63.0864 | TRUE | TRUE
Interdisciplinary Science Building | 2162038.8838 | 0 | 84603.4786 | 839087.4002 | 163476 | Lab | 158.4714 | 105.9395 | 123.4257 | 17.4862 | 88.4533 | 140.9119 | TRUE | 45.1251 | Y | 29.8651 | 45.1251 | 15.26 | 14.605 | 60.3852 | FALSE | FALSE | 0 | - | 0.058226 | 25.3631 | 25.3049 | -25.2466 | 50.668 | TRUE | TRUE | 51.7528 | Y | 36.1203 | 56.2532 | 20.1329 | 15.9874 | 76.3861 | FALSE | FALSE | 61.5934 | Y | 22.2377 | 42.6621 | 20.4244 | 1.8133 | 63.0864 | FALSE | FALSE
International House | 111982.7935 | 8468.2 | 0 | 0 | 25320 | Residential | 48.535 | 50.0816 | 60.2617 | 10.1801 | 39.9014 | 70.4419 | FALSE | 15.0903 | Y | 15.0903 | 20.7689 | 5.6787 | 9.4116 | 26.4476 | FALSE | FALSE | 33.4447 | Y | 32.5456 | 36.4687 | 3.9232 | 28.6224 | 40.3919 | FALSE | FALSE | 0 | - | 28.932 | 39.0181 | 10.086 | 18.846 | 49.1041 | TRUE | TRUE | 0 | - | 11.7772 | 14.543 | 2.7658 | 9.0114 | 17.3088 | TRUE | TRUE
Joe West Hall | 712454.9998 | 41140.315 | 0 | 0 | 130000 | Residential | 50.3456 | 50.0816 | 60.2617 | 10.1801 | 39.9014 | 70.4419 | FALSE | 18.6992 | Y | 15.0903 | 20.7689 | 5.6787 | 9.4116 | 26.4476 | FALSE | FALSE | 31.6464 | Y | 32.5456 | 36.4687 | 3.9232 | 28.6224 | 40.3919 | FALSE | FALSE | 0 | - | 28.932 | 39.0181 | 10.086 | 18.846 | 49.1041 | TRUE | TRUE | 0 | - | 11.7772 | 14.543 | 2.7658 | 9.0114 | 17.3088 | TRUE | TRUE
Koret Center | 212782.2265 | 6655.5161 | 0 | 0 | 15358 | Athletics | 90.6084 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 47.2726 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 43.3358 | Y | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | FALSE | FALSE | 0 | - | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | TRUE | TRUE | 0 | - | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | TRUE | TRUE
MacQuarrie Hall | 973759.305 | 0 | 19215.9722 | 75222.9894 | 107302 | Academic | 57.2845 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 30.9637 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 17.9083 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 8.4125 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
MacQuarrie Hall- Spartan Shops | 302468.2008 | 0 | 0 | 0 | 3724 | Food Sale | 277.1271 | 277.1271 | 277.1271 | 0 | 277.1271 | 277.1271 | FALSE | 277.1271 | #N/A | 277.1271 | 277.1271 | 0 | 277.1271 | 277.1271 | FALSE | FALSE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Modular F,A,B | 75105.5875 | 0 | 0 | 0 | 6451 | Office | 39.7241 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 39.7241 | #N/A | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 0 | #N/A | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | #N/A | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | #N/A | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE
Moss Landing Marine Lab Main Laboratory | 835644.7097 | 39083.7032 | 0 | 0 | 61062 | Lab | 110.7004 | 105.9395 | 123.4257 | 17.4862 | 88.4533 | 140.9119 | FALSE | 46.6938 | - | 29.8651 | 45.1251 | 15.26 | 14.605 | 60.3852 | FALSE | FALSE | 64.0066 | - | 0.058226 | 25.3631 | 25.3049 | -25.2466 | 50.668 | TRUE | TRUE | 0 | - | 36.1203 | 56.2532 | 20.1329 | 15.9874 | 76.3861 | TRUE | TRUE | 0 | - | 22.2377 | 42.6621 | 20.4244 | 1.8133 | 63.0864 | TRUE | TRUE
Music | 323817.9828 | 0 | 51757.7121 | 249145.2465 | 64072 | Academic | 144.6869 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 17.2441 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 80.7805 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | TRUE | TRUE | 46.6622 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Outdoor Physical Education | 213467.5865 | 0 | 0 | 0 | 123650 | Outdoor Athletics | 5.8904 | 45.7803 | 125.5599 | 79.7797 | -33.9994 | 205.3396 | FALSE | 5.8904 | Y | 45.7803 | 125.5599 | 79.7797 | -33.9994 | 205.3396 | FALSE | FALSE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Provident Credit Union Event Center | 1946272.2997 | 0 | 73314.9124 | 389189.8179 | 110140 | Athletics | 169.2614 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 60.2931 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 0 | - | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | TRUE | TRUE | 66.5652 | Y | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | FALSE | FALSE | 42.4031 | Y | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | FALSE | FALSE
Reid Hillview Airport | 14553.78 | 322.74 | 0 | 0 | 8420 | Academic | 9.7306 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 5.8976 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 3.833 | Y | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | FALSE | FALSE | 0 | - | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | TRUE | TRUE | 0 | - | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | TRUE | TRUE
Science | 571127.6285 | 0 | 29825.5985 | 0 | 89180 | Academic | 55.2954 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 21.8512 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 33.4443 | - | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 0 | Y(Will) | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | TRUE | TRUE
SC_Track & Field | 34796.5455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Simpkins Athletics Building | 58956.0863 | 3878.2968 | 0 | 0 | 22495 | Athletics | 26.1831 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 8.9424 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 17.2407 | Y | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | FALSE | FALSE | 0 | - | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | TRUE | TRUE | 0 | - | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | TRUE | TRUE
Simpkins Center Storage Building | 1029.5651 | 0 | 0 | 0 | 768 | Storage | 4.5741 | 3.4305 | 58.8408 | 55.4102 | -51.9797 | 114.251 | FALSE | 4.5741 | Y | 14.1744 | 39.2622 | 25.0877 | -10.9133 | 64.3499 | FALSE | FALSE | 0 | - | 47.3396 | 47.3396 | 0 | 47.3396 | 47.3396 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Simpkins Stadium Center | 208983.843 | 11511.9455 | 0 | 0 | 22203 | Office | 83.9638 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 32.1152 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 51.8486 | Y | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | - | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | - | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE
Spartan Recreation and Aquatic Center | 1367794.0219 | 0 | 206999.6299 | 200168.2186 | 121426 | Athletics | 228.6899 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | TRUE | 38.4342 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 0 | - | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | TRUE | TRUE | 170.4739 | Y | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | FALSE | FALSE | 19.7817 | Y | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | FALSE | FALSE
SPX Central & east | 1039713.4059 | 0 | 6770.7176 | 47185.88 | 115492 | Athletics | 41.4817 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 30.7164 | #N/A | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 0 | #N/A | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | TRUE | TRUE | 5.8625 | #N/A | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | FALSE | FALSE | 4.9028 | #N/A | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | FALSE | FALSE
SPX East-Pool | 0 | 0 | 13865.3708 | 0 | 0 | Athletics | 0 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 0 | #N/A | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | TRUE |  | 0 | #N/A | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | TRUE | TRUE | 0 | #N/A | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | TRUE | TRUE | 0 | #N/A | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | TRUE | TRUE
Storage Building | 50304.7555 | 0 | 0 | 0 | 3135 | Storage | 54.7495 | 3.4305 | 58.8408 | 55.4102 | -51.9797 | 114.251 | FALSE | 54.7495 | Y | 14.1744 | 39.2622 | 25.0877 | -10.9133 | 64.3499 | FALSE | FALSE | 0 | - | 47.3396 | 47.3396 | 0 | 47.3396 | 47.3396 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE | 0 | - | 0 | 0 | 0 | 0 | 0 | TRUE | TRUE
Student Services Center | 1369777.2571 | 17279.071 | 0 | 0 | 99853 | Office | 64.1101 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 46.8056 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 17.3045 | Y | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | FALSE | FALSE | 0 | - | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | - | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE
Student Wellness Center | 231759.5538 | 0 | 14590.8967 | 39310.3339 | 52700 | Office | 51.6428 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 15.005 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 0 | - | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 27.6867 | Y | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | FALSE | FALSE | 8.9511 | Y | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | FALSE | FALSE
Sweeney Hall | 427748.4655 | 0 | 29.3529 | 54890.3533 | 101932 | Academic | 20.8089 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 14.3182 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 0.028797 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | TRUE | TRUE | 6.462 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Washburn Hall (Student Residence) | 239415.0831 | 15533.3 | 0 | 0 | 39332 | Residential | 60.2617 | 50.0816 | 60.2617 | 10.1801 | 39.9014 | 70.4419 | FALSE | 20.7689 | Y | 15.0903 | 20.7689 | 5.6787 | 9.4116 | 26.4476 | FALSE | FALSE | 39.4928 | Y | 32.5456 | 36.4687 | 3.9232 | 28.6224 | 40.3919 | FALSE | FALSE | 0 | - | 28.932 | 39.0181 | 10.086 | 18.846 | 49.1041 | TRUE | TRUE | 0 | - | 11.7772 | 14.543 | 2.7658 | 9.0114 | 17.3088 | TRUE | TRUE
Washington Square Hall | 960582.6345 | 0 | 24394.4412 | 143283.9846 | 71857 | Academic | 103.4883 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 45.6115 | Y | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | - | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 33.9486 | Y | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 23.9282 | Y | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Yoshihiro Uchida Hall | 398814.4569 | 0 | 8718.5769 | 59043.9386 | 76871 | Athletics | 38.2607 | 35.2413 | 110.2717 | 75.0304 | -39.7891 | 185.3021 | FALSE | 17.7018 | Y | 22.3861 | 42.8534 | 20.4673 | 1.9187 | 63.3208 | FALSE | FALSE | 0 | - | 25.2888 | 38.3364 | 13.0476 | 12.2413 | 51.3839 | TRUE | TRUE | 11.3418 | Y | 9.972 | 92.5424 | 82.5704 | -72.5984 | 175.1128 | FALSE | FALSE | 9.2171 | Y | 8.1385 | 25.4371 | 17.2986 | -9.1601 | 42.7357 | FALSE | FALSE
Dudley Moorehead Hall + IRC | 342318.5 | 0 | 17043.15 | 26575.5047 | 77536 | Academic | 41.1578 | 42.2196 | 103.3342 | 61.1146 | -18.895 | 164.4489 | FALSE | 15.0639 | #N/A | 14.691 | 30.9858 | 16.2948 | -1.6038 | 47.2805 | FALSE | FALSE | 0 | #N/A | 2.3208 | 5.5118 | 3.191 | -0.8702 | 8.7028 | TRUE | TRUE | 21.981 | #N/A | 20.9628 | 37.5986 | 16.6358 | 4.327 | 54.2344 | FALSE | FALSE | 4.113 | #N/A | 7.9249 | 35.3416 | 27.4168 | -19.4919 | 62.7584 | FALSE | FALSE
Student Union | 3053825.1598 | 14395.8667 | 28827.0801 | 348116.3765 | 226256 | Office | 83.6192 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 46.0525 | Y | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | FALSE | FALSE | 6.3626 | Y | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | FALSE | FALSE | 12.7409 | Y | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | FALSE | FALSE | 18.4631 | Y | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | FALSE | FALSE
Spartan Athletic Center | 0 | 0 | 0 | 0 | 55234 | Office | 0 | 8.8203 | 69.2755 | 60.4552 | -51.6348 | 129.7306 | FALSE | 0 | N | 15.2846 | 46.2408 | 30.9562 | -15.6717 | 77.197 | TRUE | TRUE | 0 | - | 6.5666 | 25.9405 | 19.374 | -12.8074 | 45.3145 | TRUE | TRUE | 0 | - | 16.4774 | 23.9503 | 7.4729 | 9.0045 | 31.4232 | TRUE | TRUE | 0 | - | 11.3291 | 16.0851 | 4.756 | 6.5731 | 20.8411 | TRUE | TRUE
[5 empty] | Unique Program types | Unique Program types | [7 empty] | Mean | Median | Count | [6 empty] | Mean | Median | Count | [6 empty] | Mean | Median | Count | [6 empty] | Mean | Median | Count
[5 empty] | Office | Office | [7 empty] | 33.2663 | 35.9196 | 7 | [6 empty] | 10.1006 | 6.6345 | 2 | [6 empty] | 20.2138 | 20.2138 | 1 | [6 empty] | 13.7071 | 13.7071 | 1
[5 empty] | Storage | Storage | [7 empty] | 27.6995 | 23.7748 | 3 | [6 empty] | 47.3396 | 47.3396 | 1 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
[5 empty] | Lab | Lab | [7 empty] | 39.9024 | 41.5254 | 4 | [6 empty] | 4.1879 | 0.075595 | 3 | [6 empty] | 56.2567 | 51.7528 | 3 | [6 empty] | 35.3563 | 23.7307 | 3
[5 empty] | Academic | Academic | [7 empty] | 23.2825 | 21.8512 | 14 | [6 empty] | 3.944 | 3.833 | 3 | [6 empty] | 31.9855 | 33.6964 | 9 | [6 empty] | 21.5632 | 18.6688 | 11
[5 empty] | Food Service | Food Service | [7 empty] | 129.8267 | 129.8267 | 1 | [6 empty] | 155.3999 | 155.3999 | 1 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
[5 empty] | Residential | Residential | [7 empty] | 17.494 | 18.6992 | 5 | [6 empty] | 34.8613 | 33.4447 | 3 | [6 empty] | 33.9751 | 33.9751 | 2 | [6 empty] | 13.1601 | 13.1601 | 2
[5 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
[5 empty] | Outdoor Athletics | Outdoor Athletics | [7 empty] | 85.6701 | 85.6701 | 2 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
[5 empty] | Warehouse | Warehouse | [7 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
[5 empty] | Library | Library | [7 empty] | 28.6094 | 28.6094 | 2 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | 13.668 | 13.668 | 1 | [6 empty] | 29.274 | 29.274 | 1
[5 empty] | Athletics | Athletics | [7 empty] | 28.8039 | 28.8934 | 7 | [6 empty] | 31.3045 | 33.337 | 3 | [6 empty] | 63.5609 | 38.9535 | 4 | [6 empty] | 19.0762 | 14.4994 | 4
[5 empty] | Theater | Theater | [7 empty] | 68.1435 | 68.1435 | 1 | [6 empty] | 18.5483 | 18.5483 | 1 | [6 empty] | #VALUE! | #VALUE! | 0 | [6 empty] | #VALUE! | #VALUE! | 0
Food Sale
Note on G10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This does not include garage
Note on P10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This divided by area with garage

## BPD vs SJSU EUIs
Source | BPD1 | [5 empty] | SJSU
Heating Type | Gas |  | Electric |  | All |  | Electric |  |  | Gas |  |  | Steam |  |  | CHW |  |  | Total |  | SJSU Steam |  | BPD All |  | % of ALL
Site EUI | Mean | Median | Mean | Median | Mean | Median | Count | Mean | Median | Count | Mean | Median | Count | Mean | Median | Count | Mean | Median | Mean | Median | Mean | Median | Mean | Median | Mean | Median
Academic |  |  |  |  | 54 | 39 | 14 | 23.2825 | 21.8512 | 3 | 3.944 | 3.833 | 9 | 31.9855 | 33.6964 | 11 | 21.5632 | 18.6688 | 80.7752 | 78.0495 | 31.9855 | 33.6964 | 54 | 39 | 59.23% | 86.4%
Athletics | 160 | 138 |  |  | 102 | 69 | 7 | 28.8039 | 28.8934 | 3 | 31.3045 | 33.337 | 4 | 63.5609 | 38.9535 | 4 | 19.0762 | 14.4994 | 142.7454 | 115.6833 | 63.5609 | 38.9535 | 102 | 69 | 62.31% | 56.45%
Auditorium |  |  |  |  | 49 | 38 |  |  | 34 | [5 empty] | 20 |  |  | 30 | 0 | 84 |  | 20 | 49 | 38 | 0% | 52.63%
Food Service | 427 | 435 |  |  | 259 | 231 | 1 | 129.8267 | 129.8267 | 1 | 155.3999 | 155.3999 | 0 |  |  | 0 |  |  | 285.2267 | 285.2267 |  |  | 259 | 231 | 0% | 0%
Infrastructure | [18 empty] | 0 | 0 |  |  | 0 | 0 | 0% | 0%
Lab | 296 | 210 |  |  | 200 | 173 | 4 | 39.9024 | 41.5254 | 3 | 4.1879 | 0.075595 | 3 | 56.2567 | 51.7528 | 3 | 35.3563 | 23.7307 | 135.7033 | 117.0845 | 56.2567 | 51.7528 | 200 | 173 | 28.13% | 29.91%
Library |  |  |  |  | 45 | 41 | 2 | 28.6094 | 28.6094 | 0 |  |  | 1 | 13.668 | 13.668 | 1 | 29.274 | 29.274 | 71.5513 | 71.5513 | 13.668 | 13.668 | 45 | 41 | 30.37% | 33.34%
Office | 79 | 66 | 62 | 44 | 62 | 49 | 7 | 33.2663 | 35.9196 | 2 | 10.1006 | 6.6345 | 1 | 20.2138 | 20.2138 | 1 | 13.7071 | 13.7071 | 77.2878 | 76.4751 | 20.2138 | 20.2138 | 62 | 49 | 32.6% | 41.25%
Outdoor Athletics | [6 empty] | 2 | 85.6701 | 85.6701 | 0 |  |  | 0 |  |  | 0 |  |  | 85.6701 | 85.6701 |  |  | 0 | 0 | 0% | 0%
Parking | [8 empty] | 2.2423 | [9 empty] | 0 | 2.2423 |  |  | 0 | 0 | 0% | 0%
Residential | 88 | 76 |  |  | 55 | 50 | 5 | 17.494 | 18.6992 | 3 | 34.8613 | 33.4447 | 2 | 33.9751 | 33.9751 | 2 | 13.1601 | 13.1601 | 99.4905 | 99.2791 | 33.9751 | 33.9751 | 55 | 50 | 61.77% | 67.95%
Storage | [6 empty] | 3 | 27.6995 | 23.7748 | 1 | 47.3396 | 47.3396 | 0 |  |  | 0 |  |  | 75.0391 | 71.1144 |  |  | 0 | 0 | 0% | 0%
Theater |  |  |  |  | 59 | 58 | [12 empty] | 0 | 0 |  |  | 59 | 58 | 0% | 0%
Warehouse |  |  |  |  | 29 | 12 | 0 |  | 9 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 9 |  |  | 29 | 12 | 0% | 0%
Data Center | [8 empty] | 32 | [8 empty] | 200 |  |  | 0 | 0 | 0 | 0 | 0% | 0%
BPD
missing SJSU data
guess

## Climate Normalization
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan
total campus | 329955.4952 | 318945.9619 | 364757.7472 | 612730.9113 | 723291.2539 | 788639.9171 | 1234690.7124 | 1273257.6604 | 1107860.662 | 1004117.8541 | 566473.9802 | 443989.7178
total metered bldgs | 2971360.0422 | 2965075.4798 | 3267940.7462 | 3247047.2537 | 3160843.9461 | 2742364.8549 | 3025186.2538 | 3172396.2184 | 3397666.0949 | 3554832.9591 | 3300110.7697 | 3193494.6722
2017 | 0 | 0 | 2 | 1 | 69 | 137 | 210 | 221 | 264 | 81 | 2 | 0 | 987 | San Jose
2018 | 0 | 0 | 5 | 6 | 22 | 120 | 227 | 3 | 91 | 48 | 8 | 0 | 530 | 280
2019 | 0 | 0 | 0 | 19 | 3 | 130 | 157 | 248 | 159 | 50 | 0 | 0 | 766
2020 | 0 | 0 | 0 | 17 | 81 | 165 | 152 | 278 | 219 | 157 | 1 | 0 | 1070
2021 | 0 | 0 | 0 | 2 | 31 | 99 | 121 | 175 | 157 | 49 | 0 | 0 | 634
2022 | 0 | 0 | 2 | 14 | 48 | 170 | 145 | 227 | 241 | 45 | 0 | M | M
2023 | 0 | 0 | 0 | 13 | 23 | 32 | 172 | 276 | 142 | 142 | 10 | 0 | 810 | 0
2024 | 0 | 0 | 0 | 15 | 55 | 168 | 335 | M | M | M | M | M | M
Mean | 0 | 0 | 1 | 11 | 42 | 128 | 190 | 238 | 182 | 82 | 3 | 0 | 853
2017 | 0 | 0 | 0 | 2 | 21 | 27 | 30 | 48 | 159 | 55 | 0 | 0 | 342 | SF AP
2018 | 0 | 0 | 4 | 0 | 7 | M | M | 6 | 7 | 20 | 5 | 0 | M
2019 | 0 | 0 | 0 | 9 | 0 | 65 | 29 | 114 | 116 | 51 | 0 | 0 | 384
2020 | 0 | 0 | 0 | 0 | 23 | 38 | 9 | 95 | 131 | 100 | 3 | 0 | 399
2021 | 0 | 0 | 3 | 6 | 3 | 57 | 27 | 40 | 36 | 23 | 0 | 0 | 195
2022 | 0 | 0 | 2 | 9 | 9 | 45 | 19 | 69 | 114 | 13 | 0 | 0 | 280
2023 | 0 | 0 | 0 | 2 | 3 | 1 | 22 | 111 | 48 | 86 | 7 | 0 | 280
2024 | 0 | 0 | 1 | 0 | 10 | 6 | 43 | M | M | M | M | M | M
Mean | 0 | 0 | 1 | 4 | 10 | 34 | 26 | 69 | 87 | 50 | 2 | 0 | 313
2017 | 0 | 0 | 1 | 0 | 11 | 16 | 4 | 12 | 126 | 61 | 0 | 0 | 231 | SF Downtown
2018 | 0 | 2 | 6 | 0 | 1 | 4 | 2 | 0 | 6 | 22 | 6 | 0 | 49
2019 | 0 | 0 | 0 | 3 | 0 | 53 | 1 | 30 | 69 | 55 | 0 | 0 | 211
2020 | 0 | 0 | 0 | 0 | 7 | 13 | 0 | 39 | 79 | 91 | 2 | 0 | 231
2021 | 0 | 0 | 2 | 2 | 0 | 6 | 0 | 11 | 20 | 22 | 0 | 0 | 63
2022 | 0 | 1 | 0 | 7 | 1 | 24 | 1 | 1 | 61 | 14 | 0 | 0 | 110
2023 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 38 | 2 | M | M | 0 | M
2024 | 0 | 0 | 2 | 0 | 4 | M | 12 | M | M | M | M | M | M
Mean | 0 | 0 | 1 | 2 | 3 | 17 | 3 | 19 | 52 | 44 | 1 | 0 | 149
Month | 2018 CDD | 2023 CDD
1 | 0 | 0
2 | 0 | 0
3 | 5 | 0
4 | 6 | 13
5 | 22 | 23
6 | 120 | 32
7 | 227 | 172
8 | 3 | 276
9 | 91 | 142
10 | 48 | 142
11 | 8 | 10
12 | 0 | 0
Total Usage | 530 | 810
Month | Clark Hall 2018 CHW | 2018 slope | Normalized Clark Hall 2018 CHW
1 | 7866.6352 | 95.0165 | 7866.6352
2 | 10766.6236 | 95.0165 | 10766.6236
3 | 11466.6208 | 95.0165 | 10991.5381
4 | 13249.947 | 95.0165 | 13915.0628
5 | 12074.9517 | 95.0165 | 12169.9682
6 | 24849.9006 | 95.0165 | 16488.4443
7 | 33241.5337 | 95.0165 | 28015.6235
8 | 29858.2139 | 95.0165 | 55797.7319
9 | 22574.9097 | 95.0165 | 27420.7537
10 | 20333.252 | 95.0165 | 29264.8076
11 | 12424.9503 | 95.0165 | 12614.9834
12 | 6083.7289 | 95.0165 | 6083.7289
Total Usage | 204791.2674 |  | 231395.9012
Month | Dwight Bentel Hall 2018 CHW | 2018 slope | Normalized Dwight Bentel Hall 2018 CHW
1 | 51.6456 | 8.0987 | 51.6456
2 | 201.5897 | 8.0987 | 201.5897
3 | 154.9368 | 8.0987 | 114.4435
4 | 376.5075 | 8.0987 | 433.1981
5 | 432.3323 | 8.0987 | 440.431
6 | 1363.6206 | 8.0987 | 650.9382
7 | 2082.5 | 8.0987 | 1637.0735
8 | 1999.2 | 8.0987 | 4210.1351
9 | 1749.3 | 8.0987 | 2162.3318
10 | 999.6 | 8.0987 | 1760.8743
11 | 249.9 | 8.0987 | 266.0973
12 | 51.6456 | 8.0987 | 51.6456 | same as Jan- no data
Total Usage | 9712.778 |  | 11980.4037
Month | Student Union 2018 CHW | 2018 slope | Normalized Student Union 2018 CHW
1 | 8472.5211 | 151.4149 | 8472.5211
2 | 8204.0738 | 151.4149 | 8204.0738
3 | 10681.0286 | 151.4149 | 9923.9539
4 | 18370.9039 | 151.4149 | 19430.8085
5 | 30951.807 | 151.4149 | 31103.222
6 | 36486.5389 | 151.4149 | 23162.0238
7 | 47928.0867 | 151.4149 | 39600.2648
8 | 50471.9906 | 151.4149 | 91808.2702
9 | 37596.1209 | 151.4149 | 45318.283
10 | 38401.3 | 151.4149 | 52634.3047
11 | 14831.4674 | 151.4149 | 15134.2973
12 | 3324.3533 | 151.4149 | 3324.3533
Total Usage | 305720.1923 |  | 348116.3765
Month | Uchida 2018 CHW | 2018 slope | Normalized Uchida 2018 CHW
1 | 911.8962 | 31.9127 | 911.8962
2 | 1209.5176 | 31.9127 | 1209.5176
3 | 1958.3838 | 31.9127 | 1798.8205
4 | 2748.0662 | 31.9127 | 2971.4548
5 | 4181.6559 | 31.9127 | 4213.5686
6 | 5997.6 | 31.9127 | 3189.2861
7 | 9163 | 31.9127 | 7407.8038
8 | 7830.2 | 31.9127 | 16542.3556
9 | 7497 | 31.9127 | 9124.5455
10 | 5997.6 | 31.9127 | 8997.3898
11 | 1999.2 | 31.9127 | 2063.0253
12 | 614.2747 | 31.9127 | 614.2747
Total Usage | 50108.3944 |  | 59043.9386
Month | Music 2018 CHW | 2018 slope | Normalized Music 2018 CHW
1 | 9734.4266 | 89.1154 | 9734.4266
2 | 11382.1234 | 89.1154 | 11382.1234
3 | 14230.959 | 89.1154 | 13785.3821
4 | 19137.3208 | 89.1154 | 19761.1286
5 | 22442.7202 | 89.1154 | 22531.8356
6 | 29489.0135 | 89.1154 | 21646.8595
7 | 32153.8 | 89.1154 | 27252.4538
8 | 26656 | 89.1154 | 50984.5004
9 | 23573.9 | 89.1154 | 28118.7847
10 | 17992.8 | 89.1154 | 26369.6463
11 | 10412.5 | 89.1154 | 10590.7308
12 | 6987.3749 | 89.1154 | 6987.3749
Total Usage | 224192.9384 |  | 249145.2465
Month | Dudley Moorehead Hall + IRC 2018 CHW | 2018 slope | Normalized Dudley Moorehead Hall + IRC 2018 CHW
1 | 0 | 20.4899 | 0 |  | Dudley Moorehead Hall + IRC
2 | 352.3599 | 20.4899 | 352.3599
3 | 148.2739 | 20.4899 | 45.8243
4 | 659.7346 | 20.4899 | 803.164
5 | 1271.1588 | 20.4899 | 1291.6487
6 | 3579.4011 | 20.4899 | 1776.2885
7 | 5247.9 | 20.4899 | 4120.9546
8 | 4081.7 | 20.4899 | 9675.447
9 | 2748.9 | 20.4899 | 3793.8857
10 | 2082.5 | 20.4899 | 4008.5521
11 | 666.4 | 20.4899 | 707.3798
12 | 0 | 20.4899 | 0
Total Usage | 20838.3283 |  | 26575.5047

## Archive_Missing Bldgs-MAINcmps
[5 empty] | Split energy |  |  |  | Benchmark Energy |  |  |  | Benchmark % of total |  |  |  | EUI(kBtu/sq.ft) |  |  |  | -278050.7293
Month | Building Name | Campus Center | Area | Building Use Type | Electricity 1 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Electricity 1 (kBtu) | Gas (kBtu) | Steam (kBtu) | Chilled Water (kBtu) | Electricity 1 | Gas | Steam | Chilled Water | Electric EUI | Steam EUI | CHW EUI | Total EUI | Steam Energy Check
1 | Administration | Main campus | 39323 | Office |  |  | 46.9466 | 10570.9791 |  |  | 794867.7276 | 539005.494 |  |  | 0.15818 | 0.12655 |  | 132.0605 | 49.9401 |  | -43981.4762
2 | Administration | Main campus | 39323 | Office |  |  | 3104.9261 | 6715.5941
3 | Administration | Main campus | 39323 | Office |  |  | 5746.7075 | 8023.0943
4 | Administration | Main campus | 39323 | Office |  |  | 4282.5188 | 20006.2807
5 | Administration | Main campus | 39323 | Office |  |  | 8735.6524 | 15501.9256
6 | Administration | Main campus | 39323 | Office |  |  | 6981.2953 | 8743.5413
7 | Administration | Main campus | 39323 | Office |  |  | 5399.9816 | 25476.8659
8 | Administration | Main campus | 39323 | Office |  |  | 6666.4095 | -2546.5114
9 | Administration | Main campus | 39323 | Office |  |  | 4571.7249 | 18778.7799
10 | Administration | Main campus | 39323 | Office |  |  | 2429.3943 | 19348.4539
11 | Administration | Main campus | 39323 | Office |  |  | 1943.0581 | 18416.4287
12 | Administration | Main campus | 39323 | Office |  |  | 2021.5382 | 14614.1827
1 | Child Development Center | Main campus | 12889 | Academic |  |  | 25.6515 | 4719.0917 |  |  | 434313.3015 | 240622.5885 |  |  | 0.086428 | 0.056496 |  | 220.1449 | 68.0174 |  | -24031.3444
2 | Child Development Center | Main campus | 12889 | Academic |  |  | 1696.5221 | 2997.9725
3 | Child Development Center | Main campus | 12889 | Academic |  |  | 3139.9834 | 3581.6661
4 | Child Development Center | Main campus | 12889 | Academic |  |  | 2339.9552 | 8931.1948
5 | Child Development Center | Main campus | 12889 | Academic |  |  | 4773.1338 | 6920.3626
6 | Child Development Center | Main campus | 12889 | Academic |  |  | 3814.5585 | 3903.2877
7 | Child Development Center | Main campus | 12889 | Academic |  |  | 2950.5335 | 11373.3709
8 | Child Development Center | Main campus | 12889 | Academic |  |  | 3642.5058 | -1136.8125
9 | Child Development Center | Main campus | 12889 | Academic |  |  | 2497.9766 | 8383.2144
10 | Child Development Center | Main campus | 12889 | Academic |  |  | 1327.4136 | 8637.528
11 | Child Development Center | Main campus | 12889 | Academic |  |  | 1061.681 | 8221.4538
12 | Child Development Center | Main campus | 12889 | Academic |  |  | 1104.5623 | 6524.0568
1 | Computer Center | Main campus | 12900 | Data Center | 26186.8612 |  |  | 50598.9762 | 412800 |  |  | 2580000 | 0.11948 |  |  | 0.60576 | 54.1425 |  | 728.6736 |  | 0
2 | Computer Center | Main campus | 12900 | Data Center | 40608.9312 |  |  | 32144.8166
3 | Computer Center | Main campus | 12900 | Data Center | 31871.0174 |  |  | 38403.2883
4 | Computer Center | Main campus | 12900 | Data Center | 12274.3454 |  |  | 95761.9262
5 | Computer Center | Main campus | 12900 | Data Center | 22136.1261 |  |  | 74201.4107
6 | Computer Center | Main campus | 12900 | Data Center | 17527.5991 |  |  | 41851.7746
7 | Computer Center | Main campus | 12900 | Data Center | 5917.6436 |  |  | 121947.3914
8 | Computer Center | Main campus | 12900 | Data Center | 16235.2146 |  |  | -12189.1138
9 | Computer Center | Main campus | 12900 | Data Center | 4755.5358 |  |  | 89886.3792
10 | Computer Center | Main campus | 12900 | Data Center | 7134.7879 |  |  | 92613.1769
11 | Computer Center | Main campus | 12900 | Data Center | 11663.4554 |  |  | 88151.9513
12 | Computer Center | Main campus | 12900 | Data Center | 8388.9169 |  |  | 69952.1464
1 | Corporation Yard Offices | Main campus | 12837 | Office | 29250.9002 |  |  |  | 461100.3779 |  |  |  | 0.13346 |  |  |  | 60.7743 |  |  |  | 0
2 | Corporation Yard Offices | Main campus | 12837 | Office | 45360.4495
3 | Corporation Yard Offices | Main campus | 12837 | Office | 35600.1409
4 | Corporation Yard Offices | Main campus | 12837 | Office | 13710.5264
5 | Corporation Yard Offices | Main campus | 12837 | Office | 24726.2018
6 | Corporation Yard Offices | Main campus | 12837 | Office | 19578.4461
7 | Corporation Yard Offices | Main campus | 12837 | Office | 6610.0477
8 | Corporation Yard Offices | Main campus | 12837 | Office | 18134.844
9 | Corporation Yard Offices | Main campus | 12837 | Office | 5311.9655
10 | Corporation Yard Offices | Main campus | 12837 | Office | 7969.6061
11 | Corporation Yard Offices | Main campus | 12837 | Office | 13028.1582
12 | Corporation Yard Offices | Main campus | 12837 | Office | 9370.4766
1 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 16661.0098 |  |  |  | 262638 |  |  |  | 0.076015 |  |  |  | 15.2276 |  |  |  | 0
2 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 25836.8423
3 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 20277.4716
4 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 7809.3739
5 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 14083.7885
6 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 11151.6801
7 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 3765.0147
8 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 10329.4193
9 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 3025.6405
10 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 4539.4051
11 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 7420.704
12 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | 5337.3264
1 | Faculty Office Building | Main campus | 16496 | Office | 37588.4436 |  | 19.6941 | 4434.5262 | 592530.3291 |  | 333447.0421 | 226112.8253 | 0.17149 |  | 0.066356 | 0.053089 | 60.7743 | 132.0605 | 49.9401 | 242.7749 | -18450.2309
2 | Faculty Office Building | Main campus | 16496 | Office | 58289.7853 |  | 1302.5166 | 2817.192
3 | Faculty Office Building | Main campus | 16496 | Office | 45747.4429 |  | 2410.744 | 3365.6884
4 | Faculty Office Building | Main campus | 16496 | Office | 17618.5124 |  | 1796.5168 | 8392.6355
5 | Faculty Office Building | Main campus | 16496 | Office | 31774.0457 |  | 3664.6065 | 6503.0584
6 | Faculty Office Building | Main campus | 16496 | Office | 25158.9972 |  | 2928.6537 | 3667.9159
7 | Faculty Office Building | Main campus | 16496 | Office | 8494.1456 |  | 2265.2925 | 10687.5462
8 | Faculty Office Building | Main campus | 16496 | Office | 23303.9173 |  | 2796.559 | -1068.2616
9 | Faculty Office Building | Main campus | 16496 | Office | 6826.064 |  | 1917.8388 | 7877.6989
10 | Faculty Office Building | Main campus | 16496 | Office | 10241.2263 |  | 1019.131 | 8116.6772
11 | Faculty Office Building | Main campus | 16496 | Office | 16741.645 |  | 815.113 | 7725.6925
12 | Faculty Office Building | Main campus | 16496 | Office | 12041.3946 |  | 848.0354 | 6130.6502
1 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 18430.3992 |  | 10.0937 | 5027.5378 | 290530 |  | 170900 | 256350 | 0.084087 |  | 0.034009 | 0.060188 | 57.5264 | 130.6636 | 109.301 | 297.4911 | -9456.2076
2 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 28580.6996 |  | 667.5725 | 3193.9239
3 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 22430.9271 |  | 1235.567 | 3815.7686
4 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 8638.7247 |  | 920.7601 | 9514.9495
5 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 15579.4785 |  | 1878.2031 | 7372.6867
6 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 12335.982 |  | 1501.0087 | 4158.4118
7 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 4164.857 |  | 1161.0194 | 12116.7495
8 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 11426.3976 |  | 1433.3069 | -1211.116
9 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 3346.9618 |  | 982.9406 | 8931.1524
10 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 5021.4872 |  | 522.3303 | 9202.0883
11 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 8208.7783 |  | 417.7659 | 8758.8189
12 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | 5904.1474 |  | 434.6395 | 6950.4778
1 | Music | Main campus | 64072 | Academic | [16 empty] | 0
2 | Music | Main campus | 64072 | Academic
3 | Music | Main campus | 64072 | Academic
4 | Music | Main campus | 64072 | Academic
5 | Music | Main campus | 64072 | Academic
6 | Music | Main campus | 64072 | Academic
7 | Music | Main campus | 64072 | Academic
8 | Music | Main campus | 64072 | Academic
9 | Music | Main campus | 64072 | Academic
10 | Music | Main campus | 64072 | Academic
11 | Music | Main campus | 64072 | Academic
12 | Music | Main campus | 64072 | Academic
1 | Spartan Memorial | Main campus | 2300 | Auditorium | 4960.7862 |  | 2.7169 | 1353.2284 | 78200 |  | 46000 | 69000 | 0.022633 |  | 0.009154 | 0.0162 | 57.5264 | 130.6636 | 109.301 | 297.4911 | -2545.2636
2 | Spartan Memorial | Main campus | 2300 | Auditorium | 7692.8741 |  | 179.686 | 859.687
3 | Spartan Memorial | Main campus | 2300 | Auditorium | 6037.5813 |  | 332.5692 | 1027.0647
4 | Spartan Memorial | Main campus | 2300 | Auditorium | 2325.2273 |  | 247.8348 | 2561.0748
5 | Spartan Memorial | Main campus | 2300 | Auditorium | 4193.4231 |  | 505.5432 | 1984.4563
6 | Spartan Memorial | Main campus | 2300 | Auditorium | 3320.393 |  | 404.0164 | 1119.2916
7 | Spartan Memorial | Main campus | 2300 | Auditorium | 1121.0265 |  | 312.5038 | 3261.3837
8 | Spartan Memorial | Main campus | 2300 | Auditorium | 3075.5663 |  | 385.7935 | -325.9879
9 | Spartan Memorial | Main campus | 2300 | Auditorium | 900.8791 |  | 264.5715 | 2403.938
10 | Spartan Memorial | Main campus | 2300 | Auditorium | 1351.5998 |  | 140.5921 | 2476.864
11 | Spartan Memorial | Main campus | 2300 | Auditorium | 2209.5015 |  | 112.4472 | 2357.5522
12 | Spartan Memorial | Main campus | 2300 | Auditorium | 1589.1795 |  | 116.989 | 1870.8132
1 | Tower Hall | Main campus | 13096 | Auditorium | 28246.2853 |  | 15.4696 |  | 445264 |  | 261920 |  | 0.12887 |  | 0.052122 |  | 57.5264 | 130.6636 |  |  | -14492.5097
2 | Tower Hall | Main campus | 13096 | Auditorium | 43802.5561 |  | 1023.1164
3 | Tower Hall | Main campus | 13096 | Auditorium | 34377.4629 |  | 1893.6203
4 | Tower Hall | Main campus | 13096 | Auditorium | 13239.6418 |  | 1411.1497
5 | Tower Hall | Main campus | 13096 | Auditorium | 23876.9866 |  | 2878.5193
6 | Tower Hall | Main campus | 13096 | Auditorium | 18906.0292 |  | 2300.4342
7 | Tower Hall | Main campus | 13096 | Auditorium | 6383.0272 |  | 1779.3692
8 | Tower Hall | Main campus | 13096 | Auditorium | 17512.0073 |  | 2196.6749
9 | Tower Hall | Main campus | 13096 | Auditorium | 5129.5274 |  | 1506.4471
10 | Tower Hall | Main campus | 13096 | Auditorium | 7695.8919 |  | 800.5193
11 | Tower Hall | Main campus | 13096 | Auditorium | 12580.7093 |  | 640.2648
12 | Tower Hall | Main campus | 13096 | Auditorium | 9048.6499 |  | 666.125
1 | UPD Building | Main campus | 25391 | Office | 57856.9453 |  | 30.3136 | 6825.7186 | 912035.4987 |  | 513248.8994 | 348037.7514 | 0.26397 |  | 0.10214 | 0.081716 | 60.7743 | 132.0605 | 49.9401 | 242.7749 | -28398.9945
2 | UPD Building | Main campus | 25391 | Office | 89720.8984 |  | 2004.8617 | 4336.2828
3 | UPD Building | Main campus | 25391 | Office | 70415.4537 |  | 3710.6693 | 5180.5404
4 | UPD Building | Main campus | 25391 | Office | 27118.7954 |  | 2765.2375 | 12918.1261
5 | UPD Building | Main campus | 25391 | Office | 48907.2985 |  | 5640.6416 | 10009.6481
6 | UPD Building | Main campus | 25391 | Office | 38725.2726 |  | 4507.8471 | 5645.7355
7 | UPD Building | Main campus | 25391 | Office | 13074.3726 |  | 3486.7872 | 16450.5023
8 | UPD Building | Main campus | 25391 | Office | 35869.8936 |  | 4304.5242 | -1644.2914
9 | UPD Building | Main campus | 25391 | Office | 10506.8253 |  | 2951.9789 | 12125.5245
10 | UPD Building | Main campus | 25391 | Office | 15763.517 |  | 1568.6685 | 12493.3651
11 | UPD Building | Main campus | 25391 | Office | 25769.1022 |  | 1254.6395 | 11891.5531
12 | UPD Building | Main campus | 25391 | Office | 18534.375 |  | 1305.3144 | 9436.4294
1 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 145.9103 |  |  |  | 2470453.8518 |  |  |  | 0.49162 |  |  | 220.1449 |  |  | -136694.7022
2 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 9650.1296
3 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 17860.8027
4 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 13310.0952
5 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 27150.4622
6 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 21697.9095
7 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 16783.1766
8 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 20719.2423
9 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 14208.9496
10 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 7550.5726
11 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 6039.0368
12 | Hugh Gillis Hall | Main campus | 73315 | Academic |  |  | 6282.9534

## Archive_Missing Bldgs-OFFCampus
[5 empty] | Split energy |  |  |  | Benchmark Energy |  |  |  | Benchmark % of total |  |  |  | EUI
Month | Building Name | Campus Center | Area | Building Use Type | Electricity 1 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Electricity 1 (kBtu) | Gas (kBtu) | Steam (kBtu) | Chilled Water (kBtu) | Electricity 1 | Gas | Steam | Chilled Water | Electric EUI | Steam EUI | CHW EUI | Total EUI
1 | Administration | Main campus | 39323 | Office |  |  | 92.3451 | #N/A |  |  | 794867.7276 | 539005.494 |  |  | 0.31114 | #N/A |  | 259.7662 | #N/A
2 | Administration | Main campus | 39323 | Office |  |  | 6107.4648 | #N/A
3 | Administration | Main campus | 39323 | Office |  |  | 11303.9128 | #N/A
4 | Administration | Main campus | 39323 | Office |  |  | 8423.8183 | #N/A
5 | Administration | Main campus | 39323 | Office |  |  | 17183.2399 | #N/A
6 | Administration | Main campus | 39323 | Office |  |  | 13732.3771 | #N/A
7 | Administration | Main campus | 39323 | Office |  |  | 10621.8947 | #N/A
8 | Administration | Main campus | 39323 | Office |  |  | 13112.989 | #N/A
9 | Administration | Main campus | 39323 | Office |  |  | 8992.6937 | #N/A
10 | Administration | Main campus | 39323 | Office |  |  | 4778.6774 | #N/A
11 | Administration | Main campus | 39323 | Office |  |  | 3822.0424 | #N/A
12 | Administration | Main campus | 39323 | Office |  |  | 3976.4146 | #N/A
1 | Child Development Center | Main campus | 12889 | Academic |  |  | 50.4571 | #N/A |  |  | 434313.3015 | 240622.5885 |  |  | 0.17001 | #N/A |  | 433.0304 | #N/A
2 | Child Development Center | Main campus | 12889 | Academic |  |  | 3337.1001 | #N/A
3 | Child Development Center | Main campus | 12889 | Academic |  |  | 6176.4235 | #N/A
4 | Child Development Center | Main campus | 12889 | Academic |  |  | 4602.7486 | #N/A
5 | Child Development Center | Main campus | 12889 | Academic |  |  | 9388.8699 | #N/A
6 | Child Development Center | Main campus | 12889 | Academic |  |  | 7503.3289 | #N/A
7 | Child Development Center | Main campus | 12889 | Academic |  |  | 5803.7708 | #N/A
8 | Child Development Center | Main campus | 12889 | Academic |  |  | 7164.8972 | #N/A
9 | Child Development Center | Main campus | 12889 | Academic |  |  | 4913.5804 | #N/A
10 | Child Development Center | Main campus | 12889 | Academic |  |  | 2611.0548 | #N/A
11 | Child Development Center | Main campus | 12889 | Academic |  |  | 2088.3523 | #N/A
12 | Child Development Center | Main campus | 12889 | Academic |  |  | 2172.7008 | #N/A
1 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A | #N/A |  |  | #N/A | #N/A |  |  | #N/A | #N/A |  | #N/A
2 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
3 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
4 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
5 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
6 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
7 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
8 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
9 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
10 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
11 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
12 | Computer Center | Main campus | 12900 | Data Center | #N/A |  |  | #N/A
1 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A |  |  |  | 461100.3779 |  |  |  | #N/A |  |  |  | #N/A
2 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
3 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
4 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
5 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
6 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
7 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
8 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
9 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
10 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
11 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
12 | Corporation Yard Offices | Main campus | 12837 | Office | #N/A
1 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A |  |  |  | 262638 |  |  |  | #N/A |  |  |  | #N/A
2 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
3 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
4 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
5 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
6 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
7 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
8 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
9 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
10 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
11 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
12 | Corporation Yard Trades Building | Main campus | 29182 | Warehouse | #N/A
1 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 38.7388 | #N/A | 592530.3291 |  | 333447.0421 | 226112.8253 | #N/A |  | 0.13052 | #N/A | #N/A | 259.7662 | #N/A | #N/A
2 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 2562.0817 | #N/A
3 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 4741.9919 | #N/A
4 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 3533.7921 | #N/A
5 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 7208.3698 | #N/A
6 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 5760.7327 | #N/A
7 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 4455.8852 | #N/A
8 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 5500.8994 | #N/A
9 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 3772.4353 | #N/A
10 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 2004.6554 | #N/A
11 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 1603.3469 | #N/A
12 | Faculty Office Building | Main campus | 16496 | Office | #N/A |  | 1668.1061 | #N/A
1 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 19.8546 | #N/A | 290530 |  | 170900 | 256350 | #N/A |  | 0.066896 | #N/A | #N/A | 257.0185 | #N/A | #N/A
2 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 1313.1314 | #N/A
3 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 2430.3902 | #N/A
4 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 1811.1574 | #N/A
5 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 3694.4709 | #N/A
6 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 2952.5205 | #N/A
7 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 2283.7533 | #N/A
8 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 2819.3494 | #N/A
9 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 1933.468 | #N/A
10 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 1027.4363 | #N/A
11 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 821.7557 | #N/A
12 | Morris Dailey Auditorium | Main campus | 8545 | Auditorium | #N/A |  | 854.9463 | #N/A
1 | Music | Main campus | 64072 | Academic
2 | Music | Main campus | 64072 | Academic
3 | Music | Main campus | 64072 | Academic
4 | Music | Main campus | 64072 | Academic
5 | Music | Main campus | 64072 | Academic
6 | Music | Main campus | 64072 | Academic
7 | Music | Main campus | 64072 | Academic
8 | Music | Main campus | 64072 | Academic
9 | Music | Main campus | 64072 | Academic
10 | Music | Main campus | 64072 | Academic
11 | Music | Main campus | 64072 | Academic
12 | Music | Main campus | 64072 | Academic
1 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 5.3441 | #N/A | 78200 |  | 46000 | 69000 | #N/A |  | 0.018006 | #N/A | #N/A | 257.0185 | #N/A | #N/A
2 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 353.4467 | #N/A
3 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 654.1717 | #N/A
4 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 487.497 | #N/A
5 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 994.4158 | #N/A
6 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 794.71 | #N/A
7 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 614.7025 | #N/A
8 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 758.8652 | #N/A
9 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 520.4185 | #N/A
10 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 276.5481 | #N/A
11 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 221.1864 | #N/A
12 | Spartan Memorial | Main campus | 2300 | Auditorium | #N/A |  | 230.1201 | #N/A
1 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 30.429 |  | 445264 |  | 261920 |  | #N/A |  | 0.10252 |  | #N/A | 257.0185
2 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 2012.4948
3 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 3724.7969
4 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 2775.7656
5 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 5662.1172
6 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 4525.0097
7 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 3500.0624
8 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 4320.9127
9 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 2963.218
10 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 1574.6408
11 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 1259.4163
12 | Tower Hall | Main campus | 13096 | Auditorium | #N/A |  | 1310.2841
1 | UPD Building | Main campus | 25391 | Office | #N/A |  | 59.6275 | #N/A | 912035.4987 |  | 513248.8994 | 348037.7514 | #N/A |  | 0.2009 | #N/A | #N/A | 259.7662 | #N/A | #N/A
2 | UPD Building | Main campus | 25391 | Office | #N/A |  | 3943.6116 | #N/A
3 | UPD Building | Main campus | 25391 | Office | #N/A |  | 7298.9765 | #N/A
4 | UPD Building | Main campus | 25391 | Office | #N/A |  | 5439.2892 | #N/A
5 | UPD Building | Main campus | 25391 | Office | #N/A |  | 11095.2787 | #N/A
6 | UPD Building | Main campus | 25391 | Office | #N/A |  | 8867.0444 | #N/A
7 | UPD Building | Main campus | 25391 | Office | #N/A |  | 6858.5949 | #N/A
8 | UPD Building | Main campus | 25391 | Office | #N/A |  | 8467.1033 | #N/A
9 | UPD Building | Main campus | 25391 | Office | #N/A |  | 5806.6141 | #N/A
10 | UPD Building | Main campus | 25391 | Office | #N/A |  | 3085.6089 | #N/A
11 | UPD Building | Main campus | 25391 | Office | #N/A |  | 2467.9063 | #N/A
12 | UPD Building | Main campus | 25391 | Office | #N/A |  | 2567.585 | #N/A

## Archived-SkYSPark Data
SkySpark Data | [9 empty] | EUI annual
Timestamp | Building Name | Area | Building Use Type | Electricity 1 (kWh) | Electricity 2 (kWh) | Gas (therm) | Steam (therm) | Chilled Water (tons) | Suburban Propane: Corp Yard (1644-002486) Usage | Electric EUI(kBtu/sq.ft) | Gas EUI(kBtu/sq.ft) | Steam EUI(kBtu/sq.ft) | Chilled Water EUI(kBtu/sq.ft) | Propane EUI(kBtu/sq.ft) | Total EUI(kBtu/sq.ft) | List of meter names | Questions | Electricity 2 (kWh)_cost | Gas (therm)_cost | AS: Well Water (M) - Archived Usage - Archived | ATM PG&E SMD: ATM Electric (0161691543 / 0161691654) Usage | SJSU Main Campus Solar Duke Energy PPA (DER: 3802433) Cost | SJSU Main Campus Solar Duke Energy PPA (DER: 3802433) Usage | SJSU South Campus Solar Duke Energy PPA (DER: 3802432) Cost | SJSU South Campus Solar Duke Energy PPA (DER: 3802432) Usage | Stadium: East Side Electric (Closed) (PG&E: 4147571902-1 / 4145909668) Cost | Stadium: East Side Electric (Closed) (PG&E: 4147571902-1 / 4145909668) Usage | Stadium: South Scoreboard Electric (PG&E: 4147571902-1 / 7870442434) Cost | Stadium: South Scoreboard Electric (PG&E: 4147571902-1 / 7870442434) Usage | SC: CEFCU Stadium PG&E SMD: Stadium Concession Stand Electric (4147571902 / 4146304770) Usage | SC: CEFCU Stadium PG&E SMD: Stadium East Side Electric (4147571902 / 4145909668) Usage | SC: CEFCU Stadium PG&E SMD: Stadium South Scoreboard Electric (4147571902 / 7870442434) Usage | SC: CEFCU Stadium PG&E SMD: West Main Gate Electric (4147571902 / 4140791751) Usage | SC: CEFCU Stadium PG&E SMD: West Ticket Booth + Stadium Light Electric (4147571902 / 4144777738) Usage | West Ticket Booth + Stadium Light Electric (PG&E: 4147571902-1 / 4146948395) Cost | West Ticket Booth + Stadium Light Electric (PG&E: 4147571902-1 / 4146948395) Usage | CDC: Elec (PG&E: 8588879680-3 / 8588879609) Cost | SC: Concessions PG&E SMD: Parking Electric (2912101405 / 2912101607) Usage | Suburban Propane: Corp Yard (1644-002486) Cost | MLK: CHW Meter (M) Usage (Archived) | MLK: Steam Meter (M) Usage (Archived 2015-2021) | Duncan Electric Meter (N4) Usage | Duncan Hall: Electricity 2 (M) Usage | Eng Electric Meter (N4) Usage | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Cost | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Usage | SC: Field House PG&E SMD: Athletic Module Electric (4147571902 / 4149254333) Usage | SC: Field House PG&E SMD: Field House Electric (4147571902 / 4146143451) Usage | Golf Complex PG&E SMD: Golf Electric (4147571902 / 4148940516) Usage | HT: Aux Fire Pump Elec (PG&E: 6290092604-9 / 6290092893) Cost | HT: Aux Fire Pump Elec (PG&E: 6290092604-9 / 6290092893) Usage | HT: Elec Total (C) Cost (C) | HT: Elec Total (C) Usage (C) | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Cost | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Usage | OFF: Hammer Theater PG&E SMD: HT Gas (6290092604 / 6290092347) Usage | OFF: Hammer Theater PG&E SMD: HT Main Electric (6290092604 / 6290092168) Usage | HGH CHW Meter (N4) Usage | HGH Electric Meter (N4) Usage | HGH Steam Meter (N4) Usage | MacQuarrie Hall: Steam (M) Usage.1 | MQH: CHW-78-1-2 (M) Usage - Archived | MQH: CHW-78-2-2 (M) Usage | MQH: CHW Meter (N4) Usage | MQH: Elec Old AS House ISB Temp 1 (M) Usage | MQH: Elec Spartan Shops (M) Usage | MQH: Elec SWB PC-1 (M) Usage - Archived | MQH: Elec Total (C) Usage | MQH: Electric Meter (N4) Usage | MQH: Steam Meter (M) Usage - Archived | MQH: Steam Meter (N4) Usage | MLML: Pump House Elec (PG&E: 1003320516-1 / 1003320595) Cost | MLML: Pump House Elec (PG&E: 1003320516-1 / 1003320595) Usage | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Cost | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Usage | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Cost | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Usage | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Cost | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Usage | MLML: Small Boats Electric (PG&E: 5130218023-0 / 5130218783) Cost | MLML: Small Boats Electric (PG&E: 5130218023-0 / 5130218783) Usage | MLML: Small Boats Gas (PG&E: 7963846344-2 / 7963846005) Cost | MLML: Small Boats Gas (PG&E: 7963846344-2 / 7963846005) Usage | OFF: Marine Lab PG&E SMD: MLML Main Electric (9928867424 / 9928500055) Usage | OFF: Marine Lab PG&E SMD: MLML Main Gas (4348987890 / 4348987005) Usage | OFF: Marine Lab PG&E SMD: MLML Pump House Elec (1003320516 / 1003320595) Usage | OFF: Marine Lab PG&E SMD: MLML Sea Lion Elec A (4269991711 / 4269991931) Usage | Music: South Steam (Bamboo Grove) (M) Usage - Archived | Music: Steam 1 (M) Usage | Music: Steam 2 (M) Usage | Music 1 CHW Meter (N4) Usage | Music 1 Electric Meter (N4) Usage | Music 1 Steam Meter (N4) Usage | Music 2 CHW Meter (N4) Usage | Music 2 Electric Meter (N4) Usage | Music 2 Steam Meter (N4) Usage | SC: Physical Ed PG&E SMD: Marching Band Field Electric (4147571902 / 7953776421) Usage | SC: Physical Ed PG&E SMD: Softball/Tennis/Batting Cages Electric (4147571902 / 4143162076) Usage | EVC: Chilled Water Usage (M) | EVC: Chilled Water Usage (M) - Archived (2013-2015) | EVC: Chilled Water Usage (M) - Archived (2015-2021) | EVC: Steam (M) Usage - Estimate | SC: Simpkins Athletic PG&E SMD: Import Simpkins Athletic Electric (4147571902 / 4147571157) Usage | SRAC CHW (M) Usage | SPXEast: Steam (M) Usage - Archived | SPX East Electric Meter (N4) Usage | SPX East Steam Meter (N4) Usage | SCC: Ramp Lighting (M) Usage | Student Services PG&E SMD: SSC Gas (9817802206 / 9817802005) Usage | SWC: CHW (M) Usage | SH: CHW Mech Rm 128 Usage - Archived | SH: CHW Rm 122 Usage - Archived | SH: Elec Rm 122 Usage - Archived | SH: Steam Rm 122 Usage (M) | SH: Steam Rm 122 Usage (M) - Archived (Feb 20-Nov 21) | Sweeney Hall: Chilled Water 2 (M) Usage | Sweeney Hall CHW Meter (N4) Usage | Sweeney Hall Electric Meter (N4) Usage | Sweeney Hall Steam Meter (N4) Usage | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Cost | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Usage | WSH: NatGas (PG&E: 4564269832-3 / 4564269015) Usage | WSH: Elec (M) Usage - Archived | YUH: CHW (M) Usage - Archived | YUH: Elec (M) Usage - Archived | YUH: Steam (M) Usage - Archived | Uchida Hall CHW Meter (N4) Usage | Uchida Hall Electric Meter (N4) Usage | Uchida Hall Steam Meter (N4) Usage
2023-01-01 | Administration | 39323 | Office |  | 395100 |  |  |  |  | 0 |  |  |  |  | 0 | Admin: Electricity (M) Usage - Archived
2023-02-01 | Administration | 39323 | Office
2023-03-01 | Administration | 39323 | Office |  | 406330
2023-04-01 | Administration | 39323 | Office |  | 416980
2023-05-01 | Administration | 39323 | Office |  | 426520
2023-06-01 | Administration | 39323 | Office |  | 326470
2023-07-01 | Administration | 39323 | Office |  | 333330
2023-08-01 | Administration | 39323 | Office |  | 345640
2023-09-01 | Administration | 39323 | Office |  | 354470
2023-10-01 | Administration | 39323 | Office |  | 364250
2023-11-01 | Administration | 39323 | Office |  | 374910
2023-12-01 | Administration | 39323 | Office |  | 383780
2023-01-01 | Art Foundry | 7934 | Storage | 3966.5323 |  | 498.329 |  |  |  | 23.7748 | 47.3396 |  |  |  | 71.1144 | Art Foundry: Electric (PG&E: 5463751591-4 / 5469494524) Usage |  | 1.6909 | 1.6723
2023-02-01 | Art Foundry | 7934 | Storage | 3921.313 |  | 686.271 | [9 empty] | Art Foundry: Gas (PG&E: 5317852558-9 / 5317852005) Usage |  | 1.869 | 2.4885
2023-03-01 | Art Foundry | 7934 | Storage | 5039.4881 |  | 1198.4633 | [11 empty] | 2.2161 | 3.0538
2023-04-01 | Art Foundry | 7934 | Storage | 5100.3229 |  | 354.0117 | [11 empty] | 2.3275 | 0.7861
2023-05-01 | Art Foundry | 7934 | Storage | 5033.005 |  | 100.3831 | [11 empty] | 2.2628 | 0.22459
2023-06-01 | Art Foundry | 7934 | Storage | 4577.4181 |  | 26.129 | [11 empty] | 2.3159 | 0.10976
2023-07-01 | Art Foundry | 7934 | Storage | 5602.0297 |  | 12.9032 | [11 empty] | 2.8838 | 0.09031
2023-08-01 | Art Foundry | 7934 | Storage | 6189.0656 |  | 5.1097 | [11 empty] | 3.2061 | 0.078301
2023-09-01 | Art Foundry | 7934 | Storage | 5033.34 |  | 63.8 | [11 empty] | 2.6886 | 0.2002
2023-10-01 | Art Foundry | 7934 | Storage | 4253.5917 |  | 102.3465 | [11 empty] | 2.049 | 0.29301
2023-11-01 | Art Foundry | 7934 | Storage | 3787.004 |  | 411.8084 | [11 empty] | 1.8507 | 1.135
2023-12-01 | Art Foundry | 7934 | Storage | 2781.0176 |  | 296.3693 | [11 empty] | 1.3595 | 0.86429
2023-01-01 | Art | 85419 | Academic | 98751.931 |  | 0 | 7115.621 | 12217.2819 |  | 34.3445 | 0.0061174 | 47.2631 | 20.7447 |  | 102.3583 | Art : Electricity (M) Usage
2023-02-01 | Art | 85419 | Academic | 96352 |  | 0 | 6500.3516 | 11536.3224 | [7 empty] | Art PG&E SMD: Art Gas (4713751639 / 4713751005) Usage
2023-03-01 | Art | 85419 | Academic | 101252.3015 |  | 0 | 7061.428 | 13805.6848 | [7 empty] | Art : Steam (M) Usage
2023-04-01 | Art | 85419 | Academic | 94623.6985 |  | 1.0425 | 5075.2126 | 15674.6627 | [7 empty] | Art : Chilled Water (M) Usage
2023-05-01 | Art | 85419 | Academic | 94567 |  | 0 | 3585.1172 | 16223.3908
2023-06-01 | Art | 85419 | Academic | 66203.5714 |  | 0 | 1761.0603 | 13605.4128
2023-07-01 | Art | 85419 | Academic | 58777.4286 |  | 0 | 1209.0179 | 15184.7767
2023-08-01 | Art | 85419 | Academic | 45631.5571 |  | 1.0485 | 658.1964 | 13469.9876
2023-09-01 | Art | 85419 | Academic | 49508.5143 |  | 0 | 1186.519 | 14247.9617
2023-10-01 | Art | 85419 | Academic | 55579.4286 |  | 1.0394 | 1652.0815 | 15026.5973
2023-11-01 | Art | 85419 | Academic | 52589.3581 |  | 1.0455 | 2161.21 | 5086.183
2023-12-01 | Art | 85419 | Academic | 45972.3315 |  | 1.0496 | 2405.8105 | 1587.6335
2022-01-01 | Associated Students House | 8591 | Office | 3811.8788 | [5 empty] | 15.3777 |  |  |  |  | 15.3777 | AS House New Electric (M) Usage
2022-02-01 | Associated Students House | 8591 | Office | 3358
2022-03-01 | Associated Students House | 8591 | Office | 3000
2022-04-01 | Associated Students House | 8591 | Office | 2666.129
2022-05-01 | Associated Students House | 8591 | Office | 2764.871
2022-06-01 | Associated Students House | 8591 | Office | 3294
2022-07-01 | Associated Students House | 8591 | Office | 3048.6562
2022-08-01 | Associated Students House | 8591 | Office | 3280.3437
2022-09-01 | Associated Students House | 8591 | Office | 3361
2022-10-01 | Associated Students House | 8591 | Office | 2996
2022-11-01 | Associated Students House | 8591 | Office | 3347
2022-12-01 | Associated Students House | 8591 | Office | 3791.3939
2023-01-01 | Automated Bank Teller Facility | 1396 | Office | 2317.8417 | [5 empty] | 70.9973 |  |  |  |  | 70.9973 | ATM: Electric (PG&E: 0161691543-3 / 0161691654) Usage | Two solar electric meters -- are they for solar generation from this building? | 0.98253 |  |  | 1419.425 | 10.9839 | 94693 | 6.7859 | 38393
2023-02-01 | Automated Bank Teller Facility | 1396 | Office | 2018.4357 | [13 empty] | 0.91265 |  |  | 1943.5387 | 15.4093 | 119989 | 9.3766 | 47917
2023-03-01 | Automated Bank Teller Facility | 1396 | Office | 2246.3136 | [13 empty] | 0.97849 |  |  | 2252.1961 | 18.7478 | 161409 | 11.663 | 65898
2023-04-01 | Automated Bank Teller Facility | 1396 | Office | 2223.0582 | [13 empty] | 1.0149 |  |  | 2198.5817 | 29.5236 | 247174 | 18.3354 | 100621
2023-05-01 | Automated Bank Teller Facility | 1396 | Office | 2442.2334 | [13 empty] | 1.0941 |  |  | 2377.3857 | 28.0879 | 242148 | 18.182 | 102870
2023-06-01 | Automated Bank Teller Facility | 1396 | Office | 2448.5576 | [13 empty] | 1.2191 |  |  | 2439.4816 | 31.8078 | 265372 | 20.3186 | 111250
2023-07-01 | Automated Bank Teller Facility | 1396 | Office | 2561.0641 | [13 empty] | 1.2955 |  |  | 2568.0753 | 33.5112 | 288903 | 20.4055 | 115450
2023-08-01 | Automated Bank Teller Facility | 1396 | Office | 2773.5055 | [13 empty] | 1.4209 |  |  | 2885.5756 | 28.5943 | 246514 | 16.2745 | 92078
2023-09-01 | Automated Bank Teller Facility | 1396 | Office | 2577.4935 | [13 empty] | 1.3179 |  |  | 2523.9794 | 21.7277 | 181905.6 | 11.7223 | 64183
2023-10-01 | Automated Bank Teller Facility | 1396 | Office | 2598.4789 | [13 empty] | 1.2293 |  |  | 2611.4166 | 18.5516 | 159935 | 10.7885 | 61039
2023-11-01 | Automated Bank Teller Facility | 1396 | Office | 2441.6589 | [13 empty] | 1.184 |  |  | 2445.3049 | 11.7311 | 98008 | 7.776 | 42635
2023-12-01 | Automated Bank Teller Facility | 1396 | Office | 2399.4851 | [13 empty] | 1.1607 |  |  | 2409.1359 | 9.9906 | 86130 | 5.4908 | 31066
2023-01-01 | Boccardo Business Classroom Building | 83173 | Academic | 95210.569 |  |  | 9803.2085 | 1689.6605 |  | 45.4589 |  | 86.1736 | 34.8871 |  | 166.5196 | Boccardo Business: Electricity (M) Usage
2023-02-01 | Boccardo Business Classroom Building | 83173 | Academic | 85962.5 |  |  | 8322.1094 | 6833.06 | [7 empty] | Boccardo Business: Steam (M) Usage
2023-03-01 | Boccardo Business Classroom Building | 83173 | Academic | 91537.4121 |  |  | 9215.7303 | 1019.9991 | [7 empty] | Boccardo Business: Chilled Water (M) Usage
2023-04-01 | Boccardo Business Classroom Building | 83173 | Academic | 86044.5879 |  |  | 4037.8635 | 4961.0442
2023-05-01 | Boccardo Business Classroom Building | 83173 | Academic | 94838 |  |  | 6455.7031 | 5698.0143
2023-06-01 | Boccardo Business Classroom Building | 83173 | Academic | 96736.4634 |  |  | 6693.064 | 22904.9527
2023-07-01 | Boccardo Business Classroom Building | 83173 | Academic | 94350.5366 |  |  | 6492.6391 | 51267.2105
2023-08-01 | Boccardo Business Classroom Building | 83173 | Academic | 91171 |  |  | 2586.4241 | 58428.8569
2023-09-01 | Boccardo Business Classroom Building | 83173 | Academic | 96784.963 |  |  | 1156.9902 | 41662.8423
2023-10-01 | Boccardo Business Classroom Building | 83173 | Academic | 96859.037 |  |  | 3717.9138 | 37645.4668
2023-11-01 | Boccardo Business Classroom Building | 83173 | Academic | 89570.8392 |  |  | 5359.9798 | 6787.2498
2023-12-01 | Boccardo Business Classroom Building | 83173 | Academic | 89067.6263 |  |  | 7831.5477 | 2907.3101
2021-01-01 | Business Tower-Jazzland Tenant |  | Office | 134.2 | [11 empty] | Jazzland: Coffee Conces. (BT) (M) Usage - Archived
2021-02-01 | Business Tower-Jazzland Tenant |  | Office | 999.9999
2021-03-01 | Business Tower-Jazzland Tenant |  | Office | 715.8
2021-04-01 | Business Tower-Jazzland Tenant |  | Office | 428
2021-05-01 | Business Tower-Jazzland Tenant |  | Office | 491
2021-06-01 | Business Tower-Jazzland Tenant |  | Office | 191
2021-07-01 | Business Tower-Jazzland Tenant |  | Office | 368
2021-08-01 | Business Tower-Jazzland Tenant |  | Office | 344
2021-09-01 | Business Tower-Jazzland Tenant |  | Office | 424
2021-10-01 | Business Tower-Jazzland Tenant |  | Office | 589
2021-11-01 | Business Tower-Jazzland Tenant |  | Office | 458
2021-12-01 | Business Tower-Jazzland Tenant |  | Office | 938
2023-01-01 | Campus Village 1 | 960662 | Residential | 63615.8408 |  |  | 37563 | 26803 |  | 2.173 |  | 23.889 | 10.3943 |  | 36.4564 | CV1: Steam Estimate (M) Usage | electric meter-combination of 2018 and 2019
2023-02-01 | Campus Village 1 | 960662 | Residential | 60833.8782 |  |  | 35963 | 39259 | [7 empty] | CV1: CHW Estimate (M) Usage | campus garage area not counted, is that included in this usage?
2023-03-01 | Campus Village 1 | 960662 | Residential | 78010.4124 |  |  | 28489 | 57813 | [7 empty] | CV-A: Electric Meter (M) Usage - Archived
2023-04-01 | Campus Village 1 | 960662 | Residential | 66419.6448 |  |  | 30032 | 53645
2023-05-01 | Campus Village 1 | 960662 | Residential | 64431.5432 |  |  | 1557 | 84490
2023-06-01 | Campus Village 1 | 960662 | Residential |  |  |  | 1155 | 91714
2023-07-01 | Campus Village 1 | 960662 | Residential |  |  |  | 1189 | 121752
2023-08-01 | Campus Village 1 | 960662 | Residential |  |  |  | 1204 | 112109
2023-09-01 | Campus Village 1 | 960662 | Residential | 72435 |  |  | 13996 | 88372
2023-10-01 | Campus Village 1 | 960662 | Residential | 73542 |  |  | 21031 | 77881
2023-11-01 | Campus Village 1 | 960662 | Residential | 76719 |  |  | 24095 | 43205
2023-12-01 | Campus Village 1 | 960662 | Residential | 55804.6089 |  |  | 33219 | 35076
2023-01-01 | Campus Village A-Food Tenant |  | Food Service | 10458.9091 | [5 empty] | #DIV/0! |  |  |  |  | #DIV/0! | Campus Village A CV1: Market Electric Meter (M) Usage
2023-02-01 | Campus Village A-Food Tenant |  | Food Service | 13945
2023-03-01 | Campus Village A-Food Tenant |  | Food Service | 13020.8167
2023-04-01 | Campus Village A-Food Tenant |  | Food Service | 14584.1833
2023-05-01 | Campus Village A-Food Tenant |  | Food Service | 13604
2023-06-01 | Campus Village A-Food Tenant |  | Food Service | 8669.1429
2023-07-01 | Campus Village A-Food Tenant |  | Food Service | 9065.8571
2023-08-01 | Campus Village A-Food Tenant |  | Food Service | 13082
2023-09-01 | Campus Village A-Food Tenant |  | Food Service | 15325
2023-10-01 | Campus Village A-Food Tenant |  | Food Service | 15584
2023-11-01 | Campus Village A-Food Tenant |  | Food Service | 12983.4552
2023-12-01 | Campus Village A-Food Tenant |  | Food Service | 10577.0965
2023-01-01 | Campus Village Phase 2 | 186318 | Residential | 83762.9394 |  |  | 11923.3333 | 3923.6859 |  | 20.7839 |  | 44.0611 | 15.9259 |  | 80.7709 | CV2: Electric (M) Usage
2023-02-01 | Campus Village Phase 2 | 186318 | Residential | 97842 |  |  | 12280 | 8169.0943 | [7 empty] | CV2: Steam (M) Usage
2023-03-01 | Campus Village Phase 2 | 186318 | Residential | 103142.6776 |  |  | 12060.8344 | 9228.1118 | [7 empty] | CV2: CHW (M) Usage
2023-04-01 | Campus Village Phase 2 | 186318 | Residential | 106302.3224 |  |  | 8269.1656 | 17378.1035
2023-05-01 | Campus Village Phase 2 | 186318 | Residential | 96875 |  |  | 5990 | 17364.9588
2023-06-01 | Campus Village Phase 2 | 186318 | Residential | 70182.8571 |  |  | 3394.2857 | 17248.8873
2023-07-01 | Campus Village Phase 2 | 186318 | Residential | 75508.1429 |  |  | 2435.7143 | 30211.369
2023-08-01 | Campus Village Phase 2 | 186318 | Residential | 92632.4286 |  |  | 1550 | 46773.1336
2023-09-01 | Campus Village Phase 2 | 186318 | Residential | 105804.6786 |  |  | 2985.7143 | 37017.1661
2023-10-01 | Campus Village Phase 2 | 186318 | Residential | 112315.8929 |  |  | 4154.2857 | 36016.9014
2023-11-01 | Campus Village Phase 2 | 186318 | Residential | 104591.8241 |  |  | 7619.1425 | 15659.3276
2023-12-01 | Campus Village Phase 2 | 186318 | Residential | 85979.0207 |  |  | 9431.2023 | 8283.1558
2023-01-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 27899.0889 | [5 empty] | 141.1098 |  |  |  |  | 141.1098 | SC: CEFCU Stadium PG&E SMD: Stadium Concession Stand Electric (4147571902 / 4146304770) Usage | Is it correct to combine all electric meters( two are from 2018) | 1.546 | [16 empty] | 3.4269 | 4433.2527
2023-02-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 46542.0342 | [11 empty] | SC: CEFCU Stadium PG&E SMD: Stadium South Scoreboard Electric (4147571902 / 7870442434) Usage |  | 2.9593 | [16 empty] | 4.2035 | 7377.714
2023-03-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 49277.5047 | [11 empty] | SC: CEFCU Stadium PG&E SMD: West Main Gate Electric (4147571902 / 4140791751) Usage |  | 1.7933 | [16 empty] | 4.4224 | 6828.8379
2023-04-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 43874.3849 | [11 empty] | SC: CEFCU Stadium PG&E SMD: West Ticket Booth + Stadium Light Electric (4147571902 / 4144777738) Usage |  | 1.1197 | [16 empty] | 3.5327 | -570.9712
2023-05-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 31404.8505 | [11 empty] | 2018 :SC: CEFCU Stadium PG&E SMD: No. Main Gate Electric (4147571902 / 6595532772) Usage |  | 0.97053 | [16 empty] | 0.83594 | -6701.9032
2023-06-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 30659.1289 | [11 empty] | 2018: SC: CEFCU Stadium PG&E SMD: Stadium East Side Electric (4147571902 / 4145909668) Usage |  | 0.89414 | [16 empty] | 1.5058 | -6766.7843
2023-07-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 36575.7089 | [13 empty] | 1.3353 | [16 empty] | 2.485 | -4099.9332
2023-08-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 43618.0825 | [13 empty] | 2.3526 | [16 empty] | 3.3413 | 3869.0207
2023-09-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 42041.1644 | [13 empty] | 2.4762 | [16 empty] | 3.7394 | 5431.85
2023-10-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 48474.5951 | [13 empty] | 2.3655 | [16 empty] | 3.8255 | 6215.806
2023-11-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 45983.6579 | [13 empty] | 2.258 | [16 empty] | 4.0289 | 7770.2344
2023-12-01 | CEFCU Stadium | 11541 | Outdoor Athletics | 30950.0065 | [13 empty] | 1.7334 | [16 empty] | 2.9391 | 4584.6129
2023-01-01 | Central Classroom Building | 33407 | Academic | 22429.431 |  | 12.7062 | 797.5684 | 1408.6126 |  | 31.0078 | 0.80856 | 29.6447 | 41.7191 |  | 103.1802 | Central Classroom Bldg: Electricity (M) Usage
2023-02-01 | Central Classroom Building | 33407 | Academic | 25594.5 |  | 21.13 | 875.5664 | 781.6256 | [7 empty] | Central Classroom Bldg PG&E SMD: CCB Gas (4838752674 / 4838752005) Usage
2023-03-01 | Central Classroom Building | 33407 | Academic | 27439.3375 |  | 24.0758 | 1054.4662 | 843.9606 | [7 empty] | Central Classroom Bldg: Steam (M) Usage
2023-04-01 | Central Classroom Building | 33407 | Academic | 27463.6625 |  | 27.1062 | 849.7525 | 5577.9017 | [7 empty] | Central Classroom Bldg: Chilled Water (M) Usage
2023-05-01 | Central Classroom Building | 33407 | Academic | 26857.5 |  | 23.008 | 877.1973 | 8922.9015
2023-06-01 | Central Classroom Building | 33407 | Academic | 23764.0244 |  | 19.8186 | 795.9675 | 14833.2719
2023-07-01 | Central Classroom Building | 33407 | Academic | 24717.4756 |  | 20.9606 | 644.9309 | 16982.3499
2023-08-01 | Central Classroom Building | 33407 | Academic | 24128.1857 |  | 21.059 | 582.2706 | 16814.6362
2023-09-01 | Central Classroom Building | 33407 | Academic | 25513.2772 |  | 27.3458 | 743.2437 | 14955.5713
2023-10-01 | Central Classroom Building | 33407 | Academic | 26114.537 |  | 27.0112 | 743.3822 | 15094.4543
2023-11-01 | Central Classroom Building | 33407 | Academic | 25032.2472 |  | 24.1063 | 982.4481 | 9242.1102
2023-12-01 | Central Classroom Building | 33407 | Academic | 24544.4425 |  | 21.7879 | 956.608 | 10685.0432
2023-01-01 | Child Development Center | 12889 | Academic | 2434.888 |  | 124.1939 |  |  |  | 10.0648 | 7.1905 |  |  |  | 17.2553 | CDC: Elec (PG&E: 8588879680-3 / 8588879609) Usage |  |  | 0.41926 | [17 empty] | 1.0388
2023-02-01 | Child Development Center | 12889 | Academic | 2802.1913 |  | 156.4954 | [9 empty] | CDC: Gas (PG&E: 8588879680-3 / 8588879977) Usage |  |  | 0.58647 | [17 empty] | 1.3209
2023-03-01 | Child Development Center | 12889 | Academic | 2705.1182 |  | 136.6212 | [12 empty] | 0.37002 | [17 empty] | 1.1832
2023-04-01 | Child Development Center | 12889 | Academic | 2485.077 |  | 82.1638 | [12 empty] | 0.17151 | [17 empty] | 1.1282
2023-05-01 | Child Development Center | 12889 | Academic | 2952.3745 |  | 60.4894 | [12 empty] | 0.11397 | [17 empty] | 1.3231
2023-06-01 | Child Development Center | 12889 | Academic | 3149.441 |  | 41.0343 | [12 empty] | 0.087673 | [17 empty] | 1.5718
2023-07-01 | Child Development Center | 12889 | Academic | 4118.3941 |  | 18.2004 | [12 empty] | 0.051824 | [17 empty] | 2.0742
2023-08-01 | Child Development Center | 12889 | Academic | 5179.6239 |  | 31.0621 | [12 empty] | 0.07711 | [17 empty] | 2.6251
2023-09-01 | Child Development Center | 12889 | Academic | 4087.5645 |  | 56.8 | [12 empty] | 0.13546 | [17 empty] | 2.1283
2023-10-01 | Child Development Center | 12889 | Academic | 3258.6877 |  | 60.4261 | [12 empty] | 0.15379 | [17 empty] | 1.5589
2023-11-01 | Child Development Center | 12889 | Academic | 2455.3438 |  | 69.3739 | [12 empty] | 0.19901 | [17 empty] | 1.1932
2023-12-01 | Child Development Center | 12889 | Academic | 2391.5324 |  | 89.9273 | [12 empty] | 0.26812 | [17 empty] | 1.1785
2018-01-01 | Clark Hall | 192428 | Academic | 74519 |  |  | 874.328 | 7866.6352 |  | 16.6365 |  | 37.487 | 12.771 |  | 66.8945 | CL: Electric #1 (M) Usage - Archived
2018-02-01 | Clark Hall | 192428 | Academic | 80851.5 |  |  | 1256.8296 | 10766.6236 | [7 empty] | CL: Electric #2 (M) Usage - Archived
2018-03-01 | Clark Hall | 192428 | Academic | 82979.5 |  |  | 1835.9848 | 11466.6208 | [7 empty] | CL: Steam (M) Usage - Archived
2018-04-01 | Clark Hall | 192428 | Academic | 86780 |  |  | 1600.5704 | 13249.947 | [7 empty] | CL: Chilled Water (M) Usage - Archived
2018-05-01 | Clark Hall | 192428 | Academic | 74309 |  |  | 751.556 | 12074.9517
2018-06-01 | Clark Hall | 192428 | Academic | 71804.5 |  |  | 369.824 | 24849.9006
2018-07-01 | Clark Hall | 192428 | Academic | 69898 |  |  | 72.4672 | 33241.5337
2018-08-01 | Clark Hall | 192428 | Academic | 78990 |  |  | 756.9536 | 29858.2139
2018-09-01 | Clark Hall | 192428 | Academic | 85188 |  |  | 1164.6544 | 22574.9097
2018-10-01 | Clark Hall | 192428 | Academic | 88697 |  |  | 2771.0384 | 20333.252
2018-11-01 | Clark Hall | 192428 | Academic | 86552 |  |  | 60423.7504 | 12424.9503
2018-12-01 | Clark Hall | 192428 | Academic | 57689.6506 |  |  | 257.4364 | 6083.7289
2023-01-01 | Concession Buildings | 4320 | Storage | [13 empty] | there are no meters for this building , except parking , do we want that ? | 2.025
2023-02-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.835
2023-03-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.7325
2023-04-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.5396
2023-05-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.3846
2023-06-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.4127
2023-07-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.5036
2023-08-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.71
2023-09-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.8359
2023-10-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.8899
2023-11-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.864
2023-12-01 | Concession Buildings | 4320 | Storage | [14 empty] | 1.8979
2023-01-01 | Corporation Yard Offices | 12837 | Office |  |  | 583.2634 |  |  |  |  | 21.7167 |  |  |  | 21.7167 | CorpYard A: Gas (PG&E: 4755418303-9 / 4755418005) Usage |  |  | 1.945
2023-02-01 | Corporation Yard Offices | 12837 | Office |  |  | 698.0412 | [12 empty] | 2.5298
2023-03-01 | Corporation Yard Offices | 12837 | Office |  |  | 570.2473 | [12 empty] | 1.5202
2023-04-01 | Corporation Yard Offices | 12837 | Office |  |  | 145.896 | [12 empty] | 0.3442
2023-05-01 | Corporation Yard Offices | 12837 | Office |  |  | 19.3187 | [12 empty] | 0.070243
2023-06-01 | Corporation Yard Offices | 12837 | Office |  |  | 0.4 | [12 empty] | 0.039501
2023-07-01 | Corporation Yard Offices | 12837 | Office |  |  | 0 | [12 empty] | 0.039615
2023-08-01 | Corporation Yard Offices | 12837 | Office |  |  | 0 | [12 empty] | 0.039914
2023-09-01 | Corporation Yard Offices | 12837 | Office |  |  | 0.8 | [12 empty] | 0.041561
2023-10-01 | Corporation Yard Offices | 12837 | Office |  |  | 42.0792 | [12 empty] | 0.13358
2023-11-01 | Corporation Yard Offices | 12837 | Office |  |  | 174.2498 | [12 empty] | 0.4914
2023-12-01 | Corporation Yard Offices | 12837 | Office |  |  | 553.471 | [12 empty] | 1.5615
2018-01-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 163.2 |  |  |  |  | 5.3822 | 5.3822 | Suburban Propane: Corp Yard (1644-002486) Usage | [22 empty] | 1.2765
2018-02-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 175.6 | [29 empty] | 1.5199
2018-03-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 143.1 | [29 empty] | 1.1302
2018-04-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 198.02 | [29 empty] | 1.6075
2018-05-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 0 | [29 empty] | 0
2018-06-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 205.6 | [29 empty] | 1.6683
2018-07-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 114.6 | [29 empty] | 0.90859
2018-08-01 | Corporation Yard Trades Building | 29182 | Warehouse
2018-09-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 383.8 | [29 empty] | 3.1415
2018-10-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 160.1 | [29 empty] | 1.351
2018-11-01 | Corporation Yard Trades Building | 29182 | Warehouse
2018-12-01 | Corporation Yard Trades Building | 29182 | Warehouse | [5 empty] | 163.2 | [29 empty] | 1.4097
2023-01-01 | Dining Commons | 23925 | Food Service | 52353.3772 |  | 3716.8011 |  |  |  | 129.8267 | 155.3999 |  |  |  | 285.2267 | DC: Electric (PG&E: 0345535747-9 / 0345602583) Usage |  | 10.7808 | 12.8868
2023-02-01 | Dining Commons | 23925 | Food Service | 74900.1641 |  | 4573.1323 | [9 empty] | DC: Gas (PG&E: 0078358215-8 / 0078358005) Usage |  | 14.4021 | 16.5692
2023-03-01 | Dining Commons | 23925 | Food Service | 74200.0946 |  | 4173.6986 | [11 empty] | 14.1968 | 11.2939
2023-04-01 | Dining Commons | 23925 | Food Service | 85507.7674 |  | 3671.7639 | [11 empty] | 16.4185 | 6.8696
2023-05-01 | Dining Commons | 23925 | Food Service | 73908.45 |  | 2648.8375 | [11 empty] | 14.8542 | 4.3538
2023-06-01 | Dining Commons | 23925 | Food Service | 53123.7867 |  | 1568.8581 | [11 empty] | 13.8259 | 2.7602
2023-07-01 | Dining Commons | 23925 | Food Service | 58396.5333 |  | 1393.5806 | [11 empty] | 14.9882 | 2.499
2023-08-01 | Dining Commons | 23925 | Food Service | 92134.28 |  | 2327.1613 | [11 empty] | 20.0389 | 4.1611
2023-09-01 | Dining Commons | 23925 | Food Service | 106109.7467 |  | 3204 | [11 empty] | 22.5198 | 6.5346
2023-10-01 | Dining Commons | 23925 | Food Service | 103674.3207 |  | 3512.3154 | [11 empty] | 19.8854 | 7.751
2023-11-01 | Dining Commons | 23925 | Food Service | 83654.3559 |  | 3536.2652 | [11 empty] | 16.6131 | 9.1038
2023-12-01 | Dining Commons | 23925 | Food Service | 52384.2834 |  | 2853.0194 | [11 empty] | 11.9497 | 7.7919
2023-01-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 350.6696 |  |  | 12726.4661 | 62484.2034 |  | 0.026555 | 0 | 13.668 | 29.274 |  | 42.9685 | MLK: Main Total Electric Usage (C)
2023-02-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 333.9004 |  |  | 12056.37 | 59577.1596 | [7 empty] | MLK: Steam Meter (M) Usage
2023-03-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 352.1495 |  |  | 10945.2542 | 67979.0583 | [7 empty] | MLK: CHW Meter (M) Usage
2023-04-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 331.85 |  |  | 5662.6558 | 87620.5936
2023-05-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 338.4004 |  |  | 4223.54 | 99531.7547
2023-06-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 316.2437 |  |  | 2150.5244 | 114970.3959
2023-07-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 333.0561 |  |  | 1287.0256 | 146697.8949
2023-08-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 317.5286 |  |  | 894.3677 | 157307.5185
2023-09-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 305.7862 |  |  | 1484.6875 | 136612.1135
2023-10-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 310.485 |  |  | 2290.6848 | 124831.8004
2023-11-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 289.4914 |  |  | 5581.4674 | 83332.9225
2023-12-01 | Dr. Martin Luther King, Jr. Library | 499221 | Library | 305.8191 |  |  | 8930.2416 | 76902.4175
2023-01-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 2781.0455 | [11 empty] | MLK: Bookstore Electric (M) Usage
2023-02-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1933.75 | [11 empty] | MLK: Market Cafe Electric (M) Usage
2023-03-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1837.8918
2023-04-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1796.8582
2023-05-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1852.25
2023-06-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1293.2866
2023-07-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1344.5884
2023-08-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1198.4821
2023-09-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1659.1521
2023-10-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 1868.2407
2023-11-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 2136.0648
2023-12-01 | Dr. Martin Luther King, Jr. Library-Tenants |  | Library | 2065.5344
2023-01-01 | Duncan Hall | 345715 | Lab | 262459.823 |  | 10.0016 | 30776.5517 | 33783.1314 |  | 30.927 | 0.075595 | 69.7543 | 23.7307 |  | 124.4876 | Duncan Hall: Electricity 1 (M) Usage | there is a meter called DH: Verizon Electric (M) Usage. Is it a tenant?Is it included in elec meter 1 and 2 | [24 empty] | 1086606.9062 | 153413.4437
2023-02-01 | Duncan Hall | 345715 | Lab | 260747.6866 |  | 31.0602 | 30750 | 30563.2305 | [7 empty] | Duncan Hall: Electricity 2 (M) Usage | [25 empty] | 1040767.0195 | 155000.6866
2023-03-01 | Duncan Hall | 345715 | Lab | 280758.7921 |  | 16.4976 | 32716.4223 | 36002.6661 | [7 empty] | Duncan Hall: Steam (M) Usage | [25 empty] | 1144308.2065 | 165319.5115
2023-04-01 | Duncan Hall | 345715 | Lab | 274008.3722 |  | 14.2272 | 25953.8902 | 53678.6423 | [7 empty] | Duncan Hall PG&E SMD: DH Gas (0203358207 / 0203358005) Usage | [25 empty] | 1095087.269 | 161680.1528
2023-05-01 | Duncan Hall | 345715 | Lab | 258912.1068 |  | 9.8962 | 14236.25 | 41924.1042 | [7 empty] | Duncan Hall: Chilled Water (M) Usage | [25 empty] | 962386.0303 | 163000.1068
2023-06-01 | Duncan Hall | 345715 | Lab | 239491.5473 |  | 12.0505 | 11494.5536 | 58037.299 | [33 empty] | 825196.1135 | 154285.9759
2023-07-01 | Duncan Hall | 345715 | Lab | 239370.7086 |  | 3.3023 | 10124.5089 | 80692.1777 | [33 empty] | 855515.4961 | 151713.78
2023-08-01 | Duncan Hall | 345715 | Lab | 233172.7946 |  | 24.3843 | 8876.5179 | 94908.3315 | [33 empty] | 796085.5703 | 144371.5232
2023-09-01 | Duncan Hall | 345715 | Lab | 246823.496 |  | 19.752 | 10843.8988 | 72012.7499 | [33 empty] | 1024787.7676 | 142850.5267
2023-10-01 | Duncan Hall | 345715 | Lab | 270900.129 |  | 25.1425 | 15682.7083 | 84458.186 | [33 empty] | 1193448.5957 | 147778.3698
2023-11-01 | Duncan Hall | 345715 | Lab | 277303.3618 |  | 8.7418 | 25116.5192 | 56136.4616 | [33 empty] | 1162598.0156 | 159110.2773
2023-12-01 | Duncan Hall | 345715 | Lab | 289680.1437 |  | 86.2886 | 24579.289 | 41474.3967 | [33 empty] | 1192768.8789 | 168440.6765
2023-01-01 | Dwight Bentel Hall | 36691 | Academic | 15064.6552 |  |  | 3065.9759 | 51.6456 |  | 19.0632 | 0 | 40.781 | 3.1597 |  | 63.0039 | Dwight Bentel Hall: Electricity (M) Usage | chilled water data extracted from 2018
2023-02-01 | Dwight Bentel Hall | 36691 | Academic | 16889 |  |  | 2823.8086 | 201.5897 | [7 empty] | Dwight Bentel Hall: Steam (M) Usage
2023-03-01 | Dwight Bentel Hall | 36691 | Academic | 16249.72 |  |  | 2383.9213 | 154.9368 | [7 empty] | 2018 - DBH: Chilled Water (M) Usage - Archived
2023-04-01 | Dwight Bentel Hall | 36691 | Academic | 17378.78 |  |  | 1413.0904 | 376.5075
2023-05-01 | Dwight Bentel Hall | 36691 | Academic | 16967 |  |  | 851.0156 | 432.3323
2023-06-01 | Dwight Bentel Hall | 36691 | Academic | 16645.2857 |  |  | 421.9587 | 1363.6206
2023-07-01 | Dwight Bentel Hall | 36691 | Academic | 18801.5291 |  |  | 161.7891 | 2082.5
2023-08-01 | Dwight Bentel Hall | 36691 | Academic | 20676.7293 |  |  | 3.5178 | 1999.2
2023-09-01 | Dwight Bentel Hall | 36691 | Academic | 17616.28 |  |  | 0 | 1749.3
2023-10-01 | Dwight Bentel Hall | 36691 | Academic | 18687.9259 |  |  | 174.1016 | 999.6
2023-11-01 | Dwight Bentel Hall | 36691 | Academic | 18976.2563 |  |  | 2543.8222 | 249.9
2023-12-01 | Dwight Bentel Hall | 36691 | Academic | 11043.7523 |  |  | 1119.94 | 0
2023-01-01 | Engineering | 341415 | Academic | 286377.338 |  |  | 14567.2306 | 19374.6964 |  | 36.3857 | 0 | 35.7775 | 36.9791 |  | 109.1422 | Eng Electric Meter (N4) Usage | [27 empty] | 2863773.3799
2023-02-01 | Engineering | 341415 | Academic | 278527.3741 |  |  | 14797.5 | 19665.88 | [7 empty] | Engineering: Steam (M) Usage | [27 empty] | 2785273.7412
2023-03-01 | Engineering | 341415 | Academic | 312884.6304 |  |  | 16078.911 | 22997.6776 | [7 empty] | Engineering: Chilled Water (M) Usage | [27 empty] | 3128846.3037
2023-04-01 | Engineering | 341415 | Academic | 314388.7276 |  |  | 12523.589 | 71887.8498 | [35 empty] | 3143887.2756
2023-05-01 | Engineering | 341415 | Academic | 320838.9447 |  |  | 12476.5625 | 101593.5923 | [35 empty] | 3208389.4467
2023-06-01 | Engineering | 341415 | Academic | 275332.6112 |  |  | 3432.5076 | 109602.6089 | [35 empty] | 2753326.1118
2023-07-01 | Engineering | 341415 | Academic | 302103.009 |  |  | 4968.2736 | 148445.0115 | [35 empty] | 3021030.0898
2023-08-01 | Engineering | 341415 | Academic | 285617.0762 |  |  | 3959.558 | 170042.268 | [35 empty] | 2856170.7622
2023-09-01 | Engineering | 341415 | Academic | 323797.3443 |  |  | 4429.7186 | 130659.2451 | [35 empty] | 3237973.4434
2023-10-01 | Engineering | 341415 | Academic | 322579.452 |  |  | 5037.1296 | 117834.4791 | [35 empty] | 3225794.5195
2023-11-01 | Engineering | 341415 | Academic | 306935.4008 |  |  | 12502.0025 | 75735.6868 | [35 empty] | 3069354.0078
2023-12-01 | Engineering | 341415 | Academic | 311477.5785 |  |  | 17376.6775 | 64262.305 | [35 empty] | 3114775.7849
2023-01-01 | Field House | 15667 | Athletics | 12199.6112 |  | 456.5819 |  |  |  | 35.1067 | 32.9273 | 0 | 0 |  | 68.034 | SC: Field House PG&E SMD: Field House Electric (4147571902 / 4146143451) Usage | all three elctric meters have been summed | 0.03434 | [26 empty] | 1.6 | 5483.2312 | 0.04 | 6716.34
2023-02-01 | Field House | 15667 | Athletics | 14116.7488 |  | 1447.0149 | [9 empty] | SC: Field House PG&E SMD: Athletic Module Electric (4147571902 / 4149254333) Usage |  | 0.034335 | [26 empty] | 1.6223 | 4382.2688 | 0.16 | 9734.32
2023-03-01 | Field House | 15667 | Athletics | 16645.8946 |  | 2037.4592 | [9 empty] | Field House: Electric (PG&E: 4147571902-1 / 4142867809) Usage |  | 0.034365 | [26 empty] | 1.7065 | 3852.7242 | 0.04 | 12793.1304
2023-04-01 | Field House | 15667 | Athletics | 11947.1024 |  | 283.7025 | [9 empty] | SC: Field House PG&E SMD: Field House Gas (7088794250 / 7088794005) Usage |  | 0.034397 | [26 empty] | 1.3912 | 83.9424 | 0.28 | 11862.88
2023-05-01 | Field House | 15667 | Athletics | 7183.04 |  | 172.2586 | [11 empty] | 0.033564 | [26 empty] | 1.0288 | -4073.6 | 0.4 | 11256.24
2023-06-01 | Field House | 15667 | Athletics | 4638.6071 |  | 68.8717 | [11 empty] | 0.034269 | [26 empty] | 0.79204 | -5268.4909 | 0.92 | 9906.178
2023-07-01 | Field House | 15667 | Athletics | 7177.7379 |  | 60.1862 | [11 empty] | 0.034555 | [26 empty] | 1.188 | -3851.6677 | 0.92 | 11028.4856
2023-08-01 | Field House | 15667 | Athletics | 15955.8534 |  | 41.2479 | [11 empty] | 0.034577 | [26 empty] | 1.9323 | 5290.5586 | 0.96 | 10664.3348
2023-09-01 | Field House | 15667 | Athletics | 17787.45 |  | 13.8549 | [11 empty] | -0.00575 | [26 empty] | 2.0212 | 7645.95 | 0.56 | 10140.94
2023-10-01 | Field House | 15667 | Athletics | 17888.8231 |  | 34.876 | [11 empty] | 0.021408 | [26 empty] | 1.9269 | 7819.3031 | 0.36 | 10069.16
2023-11-01 | Field House | 15667 | Athletics | 17324.6875 |  | 283.2587 | [11 empty] | 0.054575 | [26 empty] | 1.8594 | 7894.5276 | 0.16 | 9430
2023-12-01 | Field House | 15667 | Athletics | 18335.1974 |  | 259.4029 | [11 empty] | 0.12074 | [26 empty] | 1.9347 | 7996.6774 | 381.88 | 9956.64
2023-01-01 | Golf Complex |  | Outdoor Athletics | 8213.7863 | [10 empty] | 0 | Golf: Electric (PG&E: 4147571902-1 / 4148940516) Usage | Which building is this | 1.9061 | [30 empty] | 5170.841
2023-02-01 | Golf Complex |  | Outdoor Athletics | 7195.4463 | [13 empty] | 1.8705 | [30 empty] | 6856.52
2023-03-01 | Golf Complex |  | Outdoor Athletics | 7207.3436 | [13 empty] | 1.784 | [30 empty] | 7202.198
2023-04-01 | Golf Complex |  | Outdoor Athletics | 5541.9067 | [13 empty] | 1.4395 | [30 empty] | 5803.629
2023-05-01 | Golf Complex |  | Outdoor Athletics | 4869.7212 | [13 empty] | 1.2406 | [30 empty] | 4551.758
2023-06-01 | Golf Complex |  | Outdoor Athletics | 4455.6501 | [13 empty] | 1.2588 | [30 empty] | 4410.62
2023-07-01 | Golf Complex |  | Outdoor Athletics | 5139.3362 | [13 empty] | 1.4953 | [30 empty] | 5259.876
2023-08-01 | Golf Complex |  | Outdoor Athletics | 5119.5484 | [13 empty] | 1.5202 | [30 empty] | 5010.7744
2023-09-01 | Golf Complex |  | Outdoor Athletics | 5700.5024 | [13 empty] | 1.7406 | [30 empty] | 5584.654
2023-10-01 | Golf Complex |  | Outdoor Athletics | 7119.9985 | [13 empty] | 1.9911 | [30 empty] | 7268.841
2023-11-01 | Golf Complex |  | Outdoor Athletics | 8211.0746 | [13 empty] | 2.3305 | [30 empty] | 8253.6269
2023-12-01 | Golf Complex |  | Outdoor Athletics | 8718.0531 | [13 empty] | 2.5264 | [30 empty] | 8815.9839
2023-01-01 | Hammer Theater | 52851 | Theater | 72853.9398 |  | 1539.5394 |  |  |  | 68.1435 | 18.5483 | 0 | 0 |  | 86.6918 | HT: Main Elec (PG&E: 6290092604-9 / 6290092168) Usage | This elec meter is not considered --- Does the main include it? HT: Aux Fire Pump Elec (PG&E: 6290092604-9 / 6290092893) Usage |  | 5.0938 | [30 empty] | 0.020111 | 5.7448 | 27.0504 | 72853.9398 | 11.5818 | 72848.195 | 1198.0772 | 70363.05
2023-02-01 | Hammer Theater | 52851 | Theater | 67513.4984 |  | 1948.6293 | [9 empty] | HT: Gas (PG&E: 6290092604-9 / 6290092347) Usage |  |  | 7.102 | [30 empty] | -0.0017835 | 15.0982 | 26.5386 | 67513.4984 | 12.8247 | 67498.4002 | 2308.3687 | 70710.7501
2023-03-01 | Hammer Theater | 52851 | Theater | 81000.5059 |  | 1661.9374 | [12 empty] | 4.3299 | [30 empty] | 0.046728 | 50.9261 | 27.9519 | 81000.5059 | 14.6345 | 80949.5798 | 1604.7858 | 74742
2023-04-01 | Hammer Theater | 52851 | Theater | 88848.6294 |  | 873.4655 | [12 empty] | 1.6687 | [30 empty] | 0.045148 | 42.244 | 32.6034 | 88848.6294 | 17.022 | 88806.3853 | 764.2496 | 94538.0999
2023-05-01 | Hammer Theater | 52851 | Theater | 99004.4895 |  | 589.3893 | [12 empty] | 0.97123 | [30 empty] | 0.047116 | 52.0692 | 36.9516 | 99004.4895 | 18.6863 | 98952.4203 | 623.1798 | 96440.7001
2023-06-01 | Hammer Theater | 52851 | Theater | 87662.4313 |  | 543.4194 | [12 empty] | 0.94552 | [30 empty] | 0.044152 | 38.7495 | 34.9773 | 87662.4313 | 18.0818 | 87623.6819 | 657.3468 | 90105.3
2023-07-01 | Hammer Theater | 52851 | Theater | 96533.1253 |  | 100.7775 | [12 empty] | 0.23492 | [30 empty] | 0.04329 | 31.2757 | 38.1967 | 96533.1253 | 20.5413 | 96501.8496 | 33.5496 | 98781.6
2023-08-01 | Hammer Theater | 52851 | Theater | 99021.6074 |  | 35.7386 | [12 empty] | 0.13327 | [30 empty] | 0.045985 | 39.6395 | 40.1329 | 99021.6074 | 21.664 | 98981.9679 | 26.3191 | 100605
2023-09-01 | Hammer Theater | 52851 | Theater | 91521.5424 |  | 89.4597 | [12 empty] | 0.25357 | [30 empty] | 0.030192 | 36.0474 | 35.5614 | 91521.5424 | 19.9384 | 91485.495 | 147.5581 | 90392.4
2023-10-01 | Hammer Theater | 52851 | Theater | 97234.5274 |  | 253.8024 | [12 empty] | 0.63973 | [30 empty] | 0.007075 | 35.5237 | 36.4428 | 97234.5274 | 19.3985 | 97199.0037 | 93.838 | 94773.9001
2023-11-01 | Hammer Theater | 52851 | Theater | 88614.2794 |  | 740.7143 | [12 empty] | 2.0006 | [30 empty] | 0.042656 | 29.6281 | 32.6645 | 88614.2794 | 18.1992 | 88584.6513 | 830.4007 | 89486.4001
2023-12-01 | Hammer Theater | 52851 | Theater | 85716.2473 |  | 1426.097 | [12 empty] | 3.9557 | [30 empty] | 0.040425 | 21.3273 | 33.9472 | 85716.2473 | 17.1885 | 85694.92 | 1221.4326 | 82120.2
2023-01-01 | Health Building | 42445 | Academic | 28607.203 |  |  | 2920.491 | 3871.7984 |  | 28.4308 | 0 | 36.5378 | 34.7958 |  | 99.7644 | Health: Electricity (M) Usage
2023-02-01 | Health Building | 42445 | Academic | 27489.9902 |  |  | 2547.24 | 3255.1141 | [7 empty] | Health: Steam (M) Usage
2023-03-01 | Health Building | 42445 | Academic | 29663.657 |  |  | 2671.6721 | 5646.1297 | [7 empty] | Health: Chilled Water (M) Usage
2023-04-01 | Health Building | 42445 | Academic | 28106.3625 |  |  | 1990.1529 | 11236.9894
2023-05-01 | Health Building | 42445 | Academic | 30470.0317 |  |  | 1572.885 | 14028.7612
2023-06-01 | Health Building | 42445 | Academic | 29117.1177 |  |  | 976.0071 | 16709.7598
2023-07-01 | Health Building | 42445 | Academic | 29932.87 |  |  | 709.4704 | 19793.3206
2023-08-01 | Health Building | 42445 | Academic | 26739.7164 |  |  | 166.5386 | 13280.898
2023-09-01 | Health Building | 42445 | Academic | 30128.125 |  |  | 73.6142 | 11969.8295
2023-10-01 | Health Building | 42445 | Academic | 32052.1415 |  |  | 219.0846 | 12346.0403
2023-11-01 | Health Building | 42445 | Academic | 29549.1803 |  |  | 680.4494 | 7059.5807
2023-12-01 | Health Building | 42445 | Academic | 31819.8088 |  |  | 980.8809 | 3877.3646
2023-01-01 | Hugh Gillis Hall | 73315 | Academic | 41521.3528 |  |  | 29324.3793 | 4237.2872 |  | 27.0313 | 0 | 957.2377 | 16.2501 |  | 1000.5191 | Hugh Gillis Hall : Electricity (main) (M) Usage | Does the main include mezzanine or aare they separate?
2023-02-01 | Hugh Gillis Hall | 73315 | Academic | 41570.0073 |  |  | 28130 | 5228.9076 | [7 empty] | Hugh Gillis Hall : Electricity (mezzanine) (M) Usage | miising months
2023-03-01 | Hugh Gillis Hall | 73315 | Academic | 47980.2874 |  |  | 20825.164 | 7140.064 | [7 empty] | Hugh Gillis Hall : Steam (M) Usage
2023-04-01 | Hugh Gillis Hall | 73315 | Academic | 45639.7077 |  |  | 30047.961 | 7214.2753 | [7 empty] | Hugh Gillis Hall : Chilled Water (M) Usage
2023-05-01 | Hugh Gillis Hall | 73315 | Academic | 44350.0366 |  |  | 26824.125 | 7305.41
2023-06-01 | Hugh Gillis Hall | 73315 | Academic | 42468.2319 |  |  | 19.0244 | 9466.6234
2023-07-01 | Hugh Gillis Hall | 73315 | Academic | 44341.7656 |  |  | 566628.1631 | 11782.3111
2023-08-01 | Hugh Gillis Hall | 73315 | Academic | 48935.6873 |  |  | 0 | 13633.4557
2023-09-01 | Hugh Gillis Hall | 73315 | Academic | 54626.1176 |  |  | 0 | 10639.7979
2023-10-01 | Hugh Gillis Hall | 73315 | Academic | 59338.0975 |  |  | 0 | 9489.2151
2023-11-01 | Hugh Gillis Hall | 73315 | Academic | 53488.6057 |  |  | 0 | 6660.0879
2023-12-01 | Hugh Gillis Hall | 73315 | Academic | 56571.8433 |  |  | 0 | 6484.0008
2023-01-01 | Industrial Studies | 113302 | Lab | 28101.7225 |  | 764.4623 | 230.1478 |  |  | 11.9823 | 12.4819 | 2.6921 | 0 |  | 27.1563 | Industrial Studies: Electricity (M) Usage
2023-02-01 | Industrial Studies | 113302 | Lab | 33390.0146 |  | 1681.5711 | 937.91 | [8 empty] | Industrial Studies: Steam (M) Usage
2023-03-01 | Industrial Studies | 113302 | Lab | 33956.2867 |  | 1994.67 | 1180.2857 | [8 empty] | Industrial Studies PG&E SMD: IS Gas (0328358199 / 0328358005) Usage
2023-04-01 | Industrial Studies | 113302 | Lab | 36440.6039 |  | 1807.9889 | 269.4801
2023-05-01 | Industrial Studies | 113302 | Lab | 34013.0826 |  | 1229.1097 | 55.4717
2023-06-01 | Industrial Studies | 113302 | Lab | 23341.4366 |  | 244.4169 | 57.3645
2023-07-01 | Industrial Studies | 113302 | Lab | 28939.5024 |  | 230.6865 | 38.5801
2023-08-01 | Industrial Studies | 113302 | Lab | 34460.2468 |  | 929.1771 | 0.87953
2023-09-01 | Industrial Studies | 113302 | Lab | 36044.0586 |  | 1212.4436 | 7.2731
2023-10-01 | Industrial Studies | 113302 | Lab | 39814.7922 |  | 1574.9001 | 13.5241
2023-11-01 | Industrial Studies | 113302 | Lab | 37459.2242 |  | 1598.2894 | 120.1163
2023-12-01 | Industrial Studies | 113302 | Lab | 31933.9011 |  | 874.5679 | 139.1252
2023-01-01 | Interdisciplinary Science Building | 163476 | Lab | 55682.3185 | [5 empty] | 45.1251 | 0 | 42.1622 | 58.1387 |  | 145.426 | ISB Temp Electric 2 (M) Usage | miising months
2023-02-01 | Interdisciplinary Science Building | 163476 | Lab | 58473.3276 | [11 empty] | ISB: Steam (M) Usage
2023-03-01 | Interdisciplinary Science Building | 163476 | Lab | 183932.6683 | [11 empty] | ISB: Chilled Water (M) Usage
2023-04-01 | Interdisciplinary Science Building | 163476 | Lab | 192719.1764 |  |  | 4292.6021 | 22277.1755
2023-05-01 | Interdisciplinary Science Building | 163476 | Lab | 199647.7203 |  |  | 8595.9559 | 67825.8537
2023-06-01 | Interdisciplinary Science Building | 163476 | Lab | 191985.8355 |  |  | 10371.7502 | 104291.5055
2023-07-01 | Interdisciplinary Science Building | 163476 | Lab | 198248.6108 |  |  | 9616.2627 | 153533.2748
2023-08-01 | Interdisciplinary Science Building | 163476 | Lab | 190209.9029 |  |  | 8927.2128 | 195080.3537
2023-09-01 | Interdisciplinary Science Building | 163476 | Lab | 204257.9859 |  |  | 9264.0638 | 131362.2632
2023-10-01 | Interdisciplinary Science Building | 163476 | Lab | 230914.8175 |  |  | 6662.6026 | 86088.2685
2023-11-01 | Interdisciplinary Science Building | 163476 | Lab | 234665.8189 |  |  | 5034.8303 | 22466.1165
2023-12-01 | Interdisciplinary Science Building | 163476 | Lab | 221300.7013 |  |  | 6159.718 | 9098.7303
2023-01-01 | International House | 25320 | Office | 8470.6003 |  | 948.5484 |  |  |  | 15.0903 | 33.4447 | 0 | 0 |  | 48.535 | Foundation: Int'l House Electric (PG&E: 6630417140-9 / 6630417801) Usage |  | 3.1673 | 3.3007
2023-02-01 | International House | 25320 | Office | 8602.3079 |  | 1038.8849 | [9 empty] | Foundation: Int'l House Gas (PG&E: 6672083804-5 / 6672083005) Usage |  | 3.3925 | 3.906
2023-03-01 | International House | 25320 | Office | 9671.672 |  | 964.358 | [11 empty] | 3.4533 | 2.655
2023-04-01 | International House | 25320 | Office | 9632.5278 |  | 753.8024 | [11 empty] | 3.4222 | 1.4479
2023-05-01 | International House | 25320 | Office | 9385.8527 |  | 620.0063 | [11 empty] | 3.3839 | 1.0371
2023-06-01 | International House | 25320 | Office | 8647.2547 |  | 471.6258 | [11 empty] | 4.4385 | 0.84477
2023-07-01 | International House | 25320 | Office | 9297.2929 |  | 400.5161 | [11 empty] | 4.9724 | 0.73207
2023-08-01 | International House | 25320 | Office | 10461.9071 |  | 408.6581 | [11 empty] | 5.3491 | 0.7549
2023-09-01 | International House | 25320 | Office | 10509.3267 |  | 567 | [11 empty] | 5.3196 | 1.1825
2023-10-01 | International House | 25320 | Office | 10329.2801 |  | 662.8081 | [11 empty] | 3.9441 | 1.4871
2023-11-01 | International House | 25320 | Office | 9081.9204 |  | 791.9532 | [11 empty] | 3.4568 | 2.0657
2023-12-01 | International House | 25320 | Office | 7892.8508 |  | 840.0387 | [11 empty] | 3.1551 | 2.3203
2019-01-01 | Joe West Hall | 130000 | Residential | 49745.4 |  | 4265.6995 | [9 empty] | Joe West Hall PG&E SMD: JW Electric (8262196692 / 8264358394) Usage
2019-02-01 | Joe West Hall | 130000 | Residential | 67316.1 |  | 6382.6745 | [9 empty] | Joe West Hall PG&E SMD: JW Gas (4564269832 / 4560082337) Usage
2019-03-01 | Joe West Hall | 130000 | Residential | 68645.1 |  | 5266.669
2019-04-01 | Joe West Hall | 130000 | Residential | 63880.5 |  | 3307.6366
2019-05-01 | Joe West Hall | 130000 | Residential | 59289.6 |  | 2967.1136
2019-06-01 | Joe West Hall | 130000 | Residential | 39449.25 |  | 1402.441
2019-07-01 | Joe West Hall | 130000 | Residential | 42106.5 |  | 1506.7151
2019-08-01 | Joe West Hall | 130000 | Residential | 59153.7 |  | 1522.9008
2019-09-01 | Joe West Hall | 130000 | Residential | 74686.7999 |  | 2198.0416
2019-10-01 | Joe West Hall | 130000 | Residential | 70525.35 |  | 3221.4297
2019-11-01 | Joe West Hall | 130000 | Residential | 63027.75 |  | 4157.9169
2019-12-01 | Joe West Hall | 130000 | Residential | 54628.95 |  | 4941.0768
2023-01-01 | Koret Center | 15358 | Athletics | 6278.1876 |  | 1599.9161 |  |  |  | 27.0313 | 43.3358 | 0 | 0 |  | 70.3671 | SC: Koret PG&E SMD: Koret Ctr Electric (4147571902 / 9578775038) Usage
2023-02-01 | Koret Center | 15358 | Athletics | 9043.44 |  | 1722.8 | [9 empty] | Koret Ctr: Gas (PG&E: 4147571902-1 / 9620442005) Usage
2023-03-01 | Koret Center | 15358 | Athletics | 10192.08 |  | 1344.4173
2023-04-01 | Koret Center | 15358 | Athletics | 10455.18 |  | 690.8827
2023-05-01 | Koret Center | 15358 | Athletics | 9990.6 |  | 296.2667
2023-06-01 | Koret Center | 15358 | Athletics | 11448.96 |  | 104.2636
2023-07-01 | Koret Center | 15358 | Athletics | 14388.36 |  | 71.1421
2023-08-01 | Koret Center | 15358 | Athletics | 15583.68 |  | 67.4276
2023-09-01 | Koret Center | 15358 | Athletics | 12240.24 |  | 151.9625
2023-10-01 | Koret Center | 15358 | Athletics | 11220.9 |  | 295.8478
2023-11-01 | Koret Center | 15358 | Athletics | 6088.9201 |  | 165.1381
2023-12-01 | Koret Center | 15358 | Athletics | 4741.8601 |  | 145.4516
2023-01-01 | MacQuarrie Hall | 107302 | Academic | 99102.5862 |  |  | 2243.7705 | 24.298 |  | 36.466 | 0 | 17.9083 | 8.4125 |  | 62.7868 | MacQuarrie Hall: Electricity (M) Usage | Spartan Shops is not included in the MacQuarrie Hall: Electricity (M) Usage meter? | [43 empty] | 2243.7705 |  | 156.1456 | 0.24219 | 5534.803 | 23199.0881 |  | -5534.803 | 980778.3398
2023-02-01 | MacQuarrie Hall | 107302 | Academic | 94913 |  |  | 2246.1426 | 43.5367 | [7 empty] | MacQuarrie Hall: Steam (M) Usage | [44 empty] | 2246.1426 |  | 148.7849 | 0.52051 | 2129.125 | 25904.8125 |  | -2129.125 | 934117.6362
2023-03-01 | MacQuarrie Hall | 107302 | Academic | 101673.5853 |  |  | 3244.6809 | 1326.2893 | [7 empty] | MacQuarrie Hall: Chilled Water (M) Usage | [44 empty] | 3244.6809 |  | 360.3937 | 15.665 | 2303.9106 | 27293.9195 |  | -2303.9106 | 1000308.5709
2023-04-01 | MacQuarrie Hall | 107302 | Academic | 97246.4147 |  |  | 2151.364 | 5109.3257 | [52 empty] | 2151.364 |  | 1094.9972 | 48.8994 | 1249.9644 | 29053.768 |  | -1249.9644 | 951498.6641
2023-05-01 | MacQuarrie Hall | 107302 | Academic | 94934 |  |  | 1720.498 | 5744.8874 | [52 empty] | 1720.498 |  | 1259.5058 | 65.8486 | 0.625 | 26800.5 |  | -0.625 | 951998.7764
2023-06-01 | MacQuarrie Hall | 107302 | Academic | 85041.4286 |  |  | 790.8231 | 8364.0627 | [52 empty] | 790.8231 |  | 1240.575 | 92.4922 | 0 | 19164.9107 |  | 0 | 817897.0889
2023-07-01 | MacQuarrie Hall | 107302 | Academic | 91992.5714 |  |  | 465.0656 | 11513.8042 | [52 empty] | 465.0656 |  | 1669.6781 | 126.9531 | 0 | 20535.3393 |  | 0 | 896158.0508
2023-08-01 | MacQuarrie Hall | 107302 | Academic | 101298.2571 |  |  | 339.7199 | 15554.0862 | [52 empty] | 339.7199 |  | 2682.5587 | 185.4756 | 0 | 172.5743 |  | 0 | 929779.0312
2023-09-01 | MacQuarrie Hall | 107302 | Academic | 98493.7429 |  |  | 719.7786 | 12823.7081 | [52 empty] | 719.7786 |  | 2638.1969 | 140.2275 | 0 | 232.473 |  | 0 | 969288.2188
2023-10-01 | MacQuarrie Hall | 107302 | Academic | 103234 |  |  | 971.0386 | 10158.3432 | [52 empty] | 971.0386 |  | 2489.3923 | 98.167 | 0 | 252.9966 |  | 0 | 996540.1562
2023-11-01 | MacQuarrie Hall | 107302 | Academic | 93899.1122 |  |  | 1922.9076 | 3231.8863 | [52 empty] | 1922.9076 |  | 1092.9326 | 33.2314 | 0 | 233.8549 |  | 0 | 921938.4004
2023-12-01 | MacQuarrie Hall | 107302 | Academic | 84969.1636 |  |  | 2400.1827 | 1328.7616 | [52 empty] | 2400.1827 |  | 556.0881 | 13.1973 | 0 | 194.32 |  | 0 | 848278.4751
2023-01-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 23199.0881 | [10 empty] | 0 | MQH: Elec Spartan Shops (M) Usage | [44 empty] | 2243.7705 |  | 156.1456 | 0.24219 | 5534.803 | 23199.0881 |  | -5534.803 | 980778.3398
2023-02-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 25904.8125 | [56 empty] | 2246.1426 |  | 148.7849 | 0.52051 | 2129.125 | 25904.8125 |  | -2129.125 | 934117.6362
2023-03-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 27293.9195 | [56 empty] | 3244.6809 |  | 360.3937 | 15.665 | 2303.9106 | 27293.9195 |  | -2303.9106 | 1000308.5709
2023-04-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 29053.768 | [56 empty] | 2151.364 |  | 1094.9972 | 48.8994 | 1249.9644 | 29053.768 |  | -1249.9644 | 951498.6641
2023-05-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 26800.5 | [56 empty] | 1720.498 |  | 1259.5058 | 65.8486 | 0.625 | 26800.5 |  | -0.625 | 951998.7764
2023-06-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 19164.9107 | [56 empty] | 790.8231 |  | 1240.575 | 92.4922 | 0 | 19164.9107 |  | 0 | 817897.0889
2023-07-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 20535.3393 | [56 empty] | 465.0656 |  | 1669.6781 | 126.9531 | 0 | 20535.3393 |  | 0 | 896158.0508
2023-08-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 172.5743 | [56 empty] | 339.7199 |  | 2682.5587 | 185.4756 | 0 | 172.5743 |  | 0 | 929779.0312
2023-09-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 232.473 | [56 empty] | 719.7786 |  | 2638.1969 | 140.2275 | 0 | 232.473 |  | 0 | 969288.2188
2023-10-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 252.9966 | [56 empty] | 971.0386 |  | 2489.3923 | 98.167 | 0 | 252.9966 |  | 0 | 996540.1562
2023-11-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 233.8549 | [56 empty] | 1922.9076 |  | 1092.9326 | 33.2314 | 0 | 233.8549 |  | 0 | 921938.4004
2023-12-01 | MacQuarrie Hall- Spartan Shops |  | Academic | 194.32 | [56 empty] | 2400.1827 |  | 556.0881 | 13.1973 | 0 | 194.32 |  | 0 | 848278.4751
2023-01-01 | Modular F,A,B | 6451 | Office | 6799.4327 | [5 empty] | 39.7241 | 0 | 0 | 0 |  | 39.7241 | Mod F: Electric (PG&E: 4672084975-4 / 4672084566) Usage | Mod F: Electric (PG&E: 4672084975-4 / 4672084566) & Modular F, A, B PG&E SMD: Mod F Electric (4672084975 / 4672084566) are the same meter? Only first month is different | 2.8499
2023-02-01 | Modular F,A,B | 6451 | Office | 7317.3945 | [12 empty] | Only main campus Mod A/B and F considered | 3.4299
2023-03-01 | Modular F,A,B | 6451 | Office | 7572.5787 | [13 empty] | 3.29
2023-04-01 | Modular F,A,B | 6451 | Office | 6446.9297 | [13 empty] | 2.9137
2023-05-01 | Modular F,A,B | 6451 | Office | 5945.5359 | [13 empty] | 2.6505
2023-06-01 | Modular F,A,B | 6451 | Office | 5593.1733 | [13 empty] | 2.8059
2023-07-01 | Modular F,A,B | 6451 | Office | 6015.1655 | [13 empty] | 3.0645
2023-08-01 | Modular F,A,B | 6451 | Office | 6428.5878 | [13 empty] | 3.2985
2023-09-01 | Modular F,A,B | 6451 | Office | 5866.7433 | [13 empty] | 3.0967
2023-10-01 | Modular F,A,B | 6451 | Office | 5715.5019 | [13 empty] | 2.7099
2023-11-01 | Modular F,A,B | 6451 | Office | 5548.9721 | [13 empty] | 2.6683
2023-12-01 | Modular F,A,B | 6451 | Office | 5855.572 | [13 empty] | 2.8189
2023-01-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 69646.4452 | 14562.7164 | 4720.1935 |  |  |  | 50.2825 | 68.9258 | 0 | 0 |  | 119.2083 | MLML: Main Electric (PG&E: 9928867424-7 / 9928500055) Usage | Pump house and boats electric/gas is not counted- Process loads? | 16.1934 | 14.1908 | [52 empty] | 6.3859 | 26050.67 | 0.043336 | 85.3824 | 3.7185 | 14477.334 | 1.1316 | 340.9677 | 0.41246 | 1087.1851 | 0.13324 | 37.6167 | 70026.87 |  |  | 48.835
2023-02-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 66994 | 13477.8038 | 4739.2763 | [9 empty] | MLML: Sea Lion Elec A (PG&E: 4269991711-0 / 4269991931) Usage | Main and sea lion gas is added | 16.6521 | 15.2874 | [52 empty] | 5.8838 | 23967.3043 | -0.016667 | 40.3045 | 3.7819 | 13437.4994 | 1.2145 | 336.9323 | 0.45956 | 1114.7055 | 0.21698 | 59.0333 | 67420.96 |  |  | 18.365
2023-03-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 73143.6226 | 14108.2081 | 4919.2249 | [9 empty] | MLML: Sea Lion Elec B (PG&E: 8651222183-8 / 8651222327) Usage |  | 16.5001 | 11.841 | [52 empty] | 6.7313 | 28103.5972 | 0.0086027 | 15.6705 | 3.752 | 14092.5376 | 0.78289 | 293.7619 | 0.48194 | 1272.3987 | 0.14219 | 49.9715 | 72577.08 |  |  | 29.231
2023-04-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 69803.5774 | 12865.0101 | 4257.1147 | [9 empty] | MLML: Main Gas (PG&E: 4348987890-0 / 4348987005) Usage |  | 16.3289 | 7.0651 | [52 empty] | 6.1188 | 27020.7742 | 0.01769 | 12.0401 | 3.444 | 12852.9699 | 0.37907 | 198.8069 | 0.44577 | 1123.6643 | 0.057342 | 23.5285 | 70166.2 |  |  | 10.103
2023-05-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 69574.5806 | 12786.116 | 3241.2421 | [9 empty] | MLML: Sea Lion Gas (PG&E: 7265654370-8 / 7265654005) Usage |  | 16.4788 | 4.8395 | [52 empty] | 6.7663 | 28123.5375 | 0.017141 | 10.7001 | 3.5061 | 12775.4158 | 0.20764 | 121.1313 | 0.45999 | 1186.5983 | 0.028142 | 10.9667 | 71262.54 |  |  | 11.92
2023-06-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 67851.9194 | 12016.5825 | 2128.1097 | [11 empty] | 18.733 | 3.439 | [52 empty] | 7.7393 | 26212.3693 | 0.018734 | 13.491 | 3.8966 | 12003.0915 | 0.12148 | 61.9806 | 0.54697 | 1284.9333 | 0.01988 | 5.4667 | 68657.72 |  |  | 13.158
2023-07-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 69741.4655 | 12515.7807 | 1871.4116 | [11 empty] | 20.4975 | 3.0777 | [52 empty] | 7.1526 | 25623.6694 | 0.01662 | 8.6626 | 4.2338 | 12507.1181 | 0.10995 | 53.7987 | 0.51456 | 1187.3608 | 0.017261 | 3.7356 | 69408.6701 |  |  | 8.243
2023-08-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 70459.8345 | 12295.6111 | 1693.7804 | [11 empty] | 20.9769 | 2.9683 | [52 empty] | 8.1725 | 26894.8351 | 0.025426 | 29.3874 | 4.2157 | 12266.2238 | 0.064338 | 24.8707 | 0.56323 | 1290.2458 | 0.016689 | 3.131 | 70122.9 |  |  | 34.942
2023-09-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 69127.7625 | 11529.3645 | 1199.9346 | [11 empty] | 20.5979 | 2.4183 | [52 empty] | 7.949 | 25743.5278 | -0.021155 | 23.2078 | 4.0697 | 11506.1567 | 0.067494 | 23.1346 | 0.56676 | 1242.4933 | 0.018429 | 3.55 | 69547.87 |  |  | 18.68
2023-10-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 71846.3557 | 11818.2049 | 2005.4735 | [11 empty] | 19.0666 | 4.4786 | [52 empty] | 6.9154 | 27226.4524 | 0.012576 | 19.1686 | 3.5639 | 11799.0364 | 0.035839 | 6.5809 | 0.53765 | 1233.6493 | 0.02188 | 4.8655 | 71916.52 |  |  | 18.644
2023-11-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 70198.4366 | 11917.7373 | 3940.0128 | [11 empty] | 18.3031 | 9.7667 | [52 empty] | 7.627 | 27276.5233 | 0.016422 | 6.8683 | 3.6181 | 11910.869 | 0.28995 | 103.228 | 0.49435 | 1093.6912 | 0.03677 | 9.9006 | 69202.52 |  |  | 7.868
2023-12-01 | Moss Landing Marine Lab Main Laboratory | 56704 | Lab | 67256.7097 | 12177.7649 | 4367.929 | [11 empty] | 17.7598 | 11.3709 | [52 empty] | 7.6942 | 29715.2049 | 0.01716 | 8.267 | 3.7476 | 12169.498 | 0.51007 | 179.4065 | 0.49232 | 1084.0529 | 0.06943 | 21.2258 | 67347.73 |  |  | 5.559
2023-01-01 | Music | 64072 | Academic | 15674.1034 |  |  | 6544.5801 | 0 |  | 7.7123 | 0 | 80.7805 | 0.00012193 |  | 88.4929 | Music: Electricity (M) Usage | Music: Chilled Water (M) Usage -- this usage is very low. Did some thing go offline , should we take naother year for chilled water | [71 empty] | 4068.2415 | 2476.3386 |  | 158580.8008
2023-02-01 | Music | 64072 | Academic | 14052 |  |  | 5881.3574 | 0 | [7 empty] | Music: Steam 1 (M) Usage | [72 empty] | 3676.4453 | 2204.9121 |  | 143310.3945
2023-03-01 | Music | 64072 | Academic | 13510.201 |  |  | 6260.1005 | 0 | [7 empty] | Music: Steam 2 (M) Usage | [72 empty] | 3822.6179 | 2437.4826 |  | 151671.8789
2023-04-01 | Music | 64072 | Academic | 9574.799 |  |  | 5573.4152 | 0 | [7 empty] | Music: Chilled Water (M) Usage | [72 empty] | 3040.9173 | 2532.4979 |  | 126524.6914
2023-05-01 | Music | 64072 | Academic | 9148.5 |  |  | 3726.2012 | 0 | [80 empty] | 2331.3477 | 1394.8535 |  | 132556.166
2023-06-01 | Music | 64072 | Academic | 6513.1098 |  |  | 2906.5072 | 0 | [80 empty] | 1452.2104 | 1454.2969 |  | 116282.545
2023-07-01 | Music | 64072 | Academic | 7158.8902 |  |  | 2558.1705 | 0 | [80 empty] | 1362.1646 | 1196.0059 |  | 118623.6367
2023-08-01 | Music | 64072 | Academic | 9543.35 |  |  | 2110.6468 | 0.57661 | [80 empty] | 1066.7667 | 1043.88 |  | 108481.3085
2023-09-01 | Music | 64072 | Academic | 11769.0607 |  |  | 2042.7663 | 0.074402 | [80 empty] | 497.9947 | 1544.7716 |  | 130467.2803
2023-10-01 | Music | 64072 | Academic | 14087.3393 |  |  | 2289.3604 | 0 | [80 empty] | 425.4534 | 1863.9069 |  | 139665.335
2023-11-01 | Music | 64072 | Academic | 17368.7809 |  |  | 5600.28 | 0 | [80 empty] | 3260.372 | 2339.908 |  | 170937.2139
2023-12-01 | Music | 64072 | Academic | 16423.8484 |  |  | 6264.3267 | 0 | [80 empty] | 3732.7105 | 2531.6162 |  | 167020.4121
2023-01-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 6418.8333 | [12 empty] | 2.6286
2023-02-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 5902.8333 | [12 empty] | 3.6841
2023-03-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 4736.9868 | [12 empty] | 4.3677
2023-04-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | -350.9451 | [12 empty] | 3.4958
2023-05-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 19747.825 | [12 empty] | 3.5447
2023-06-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 1398.3 | [12 empty] | 1.9795
2023-07-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | -4273.8966 | [12 empty] | 2.8281
2023-08-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 5085.6966 | [12 empty] | 2.9286
2023-09-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 7363.45 | [12 empty] | 2.5334
2023-10-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 7900.948 | [12 empty] | 4.0137
2023-11-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 8262.5439 | [12 empty] | 3.0358
2023-12-01 | Outdoor Physical Education | 123650 | Outdoor Athletics |  | 7835.2581 | [12 empty] | 2.5625
2023-01-01 | Provident Credit Union Event Center | 110140 | Athletics | 181396.9697 |  |  | 15316.1903 | 34.4973 |  | 63.1248 | 0 | 66.5652 | 0.064578 |  | 129.7546 | EVC: Electric Meter (M) Usage | what is this meter--EVC: Chilled Water Usage © © | [81 empty] | 25195.8444
2023-02-01 | Provident Credit Union Event Center | 110140 | Athletics | 167200 |  |  | 14262.96 | 37.0224 | [7 empty] | EVC: Steam (M) Usage | [82 empty] | 24879.0444
2023-03-01 | Provident Credit Union Event Center | 110140 | Athletics | 168325.6637 |  |  | 14067.9395 | 22.5942 | [7 empty] | EVC: Chilled Water Usage (M) | [82 empty] | 16787.4932
2023-04-01 | Provident Credit Union Event Center | 110140 | Athletics | 148174.3363 |  |  | 7323.0605 | 29.3978 | [90 empty] | 20839.8665
2023-05-01 | Provident Credit Union Event Center | 110140 | Athletics | 155000 |  |  | 0 | 33.9123 | [90 empty] | 25230.737
2023-06-01 | Provident Credit Union Event Center | 110140 | Athletics | 157285.7143 |  |  | 0.0085714 | 32.0185 | [90 empty] | 23053.3464
2023-07-01 | Provident Credit Union Event Center | 110140 | Athletics | 167814.2857 |  |  | 0.011429 | 66.8151 | [90 empty] | 45534.874
2023-08-01 | Provident Credit Union Event Center | 110140 | Athletics | 161820 |  |  | 0 | 91.4325 | [90 empty] | 68025.7502
2023-09-01 | Provident Credit Union Event Center | 110140 | Athletics | 183751.4286 |  |  | 0 | 102.1823 | [90 empty] | 72539.287
2023-10-01 | Provident Credit Union Event Center | 110140 | Athletics | 194828.5714 |  |  | 40.57 | 102.1823 | [90 empty] | 37976.0178
2023-11-01 | Provident Credit Union Event Center | 110140 | Athletics | 174567.4653 |  |  | 9457.8016 | 14.8967 | [90 empty] | 10740.5417
2023-12-01 | Provident Credit Union Event Center | 110140 | Athletics | 177515.2933 |  |  | 12846.3705 | 25.7656 | [90 empty] | 18387.0153
2023-01-01 | Reid Hillview Airport | 8420 | Academic | 812.72 |  | 49.5 |  |  |  | 5.8976 | 3.833 | 0 | 0 |  | 9.7306 | Reid-Hillview Airport: Electric (County of SC: 7856821607) Usage |  | 0.52844 | 0.14567
2023-02-01 | Reid Hillview Airport | 8420 | Academic | 1055.26 |  | 58.74 | [9 empty] | Reid-Hillview Airport: Gas (County of SC: 2866353030) Cost |  | 0.72766 | 0.22001
2023-03-01 | Reid Hillview Airport | 8420 | Academic | 1046.08 |  | 76.12 | [11 empty] | 0.68532 | 0.26046
2023-04-01 | Reid Hillview Airport | 8420 | Academic | 1683.24 |  | 67.76 | [11 empty] | 1.0293 | 0.18299
2023-05-01 | Reid Hillview Airport | 8420 | Academic | 1614.17 |  | 25.08 | [11 empty] | 0.95378 | 0.044919
2023-06-01 | Reid Hillview Airport | 8420 | Academic | 1850.69 |  | 8.8 | [11 empty] | 1.1014 | 0.018472
2023-07-01 | Reid Hillview Airport | 8420 | Academic | 544.5 |  | 4.84 | [11 empty] | 0.52554 | 0.01211
2023-08-01 | Reid Hillview Airport | 8420 | Academic | 859.38 |  | 0 | [11 empty] | 0.7727 | 0.0049462
2023-09-01 | Reid Hillview Airport | 8420 | Academic | 1724.45 |  | 0 | [11 empty] | 1.1787 | 0.021056
2023-10-01 | Reid Hillview Airport | 8420 | Academic | 1184.56 |  | 0.66 | [11 empty] | 0.91968 | 0.0059005
2023-11-01 | Reid Hillview Airport | 8420 | Academic | 1246 |  | 5.72 | [11 empty] | 0.90291 | 0.017864
2023-12-01 | Reid Hillview Airport | 8420 | Academic | 932.73 |  | 25.52 | [11 empty] | 0.69641 | 0.068038
2023-01-01 | Science | 89180 | Academic | 26948.2793 | [5 empty] | 21.8512 | 0 | 0 | 0 |  | 21.8512 | Science: Electricity (M) Usage
2023-02-01 | Science | 89180 | Academic | 41999.9361
2023-03-01 | Science | 89180 | Academic | 48656.649
2023-04-01 | Science | 89180 | Academic | 48143.4399
2023-05-01 | Science | 89180 | Academic | 51199.913
2023-06-01 | Science | 89180 | Academic | 51804.9263
2023-07-01 | Science | 89180 | Academic | 53895.0897
2023-08-01 | Science | 89180 | Academic | 55091.4901
2023-09-01 | Science | 89180 | Academic | 54775.235
2023-10-01 | Science | 89180 | Academic | 53633.3455
2023-11-01 | Science | 89180 | Academic | 43641.8464
2023-12-01 | Science | 89180 | Academic | 41337.4781
2018-01-01 | SC_Track & Field |  | Outdoor Athletics | 18.2623 | [10 empty] | 0 |  | not a bldg, which bldg is this
2018-02-01 | SC_Track & Field |  | Outdoor Athletics | 201.9109
2018-03-01 | SC_Track & Field |  | Outdoor Athletics | 2567.0349
2018-04-01 | SC_Track & Field |  | Outdoor Athletics | 3354.2388
2018-05-01 | SC_Track & Field |  | Outdoor Athletics | 3351.222
2018-06-01 | SC_Track & Field |  | Outdoor Athletics | 3565.0656
2018-07-01 | SC_Track & Field |  | Outdoor Athletics | 5046.8181
2018-08-01 | SC_Track & Field |  | Outdoor Athletics | 5319.7411
2018-09-01 | SC_Track & Field |  | Outdoor Athletics | 4652.906
2018-10-01 | SC_Track & Field |  | Outdoor Athletics | 4807.7849
2018-11-01 | SC_Track & Field |  | Outdoor Athletics | 1911.561
2018-12-01 | SC_Track & Field |  | Outdoor Athletics | 0
2023-01-01 | Simpkins Athletics Building | 22495 | Athletics |  | 3086.7957 | 796.7 |  |  |  | 0 | 17.2407 | 0 | 0 |  | 17.2407 | Simpkins Athletic: Electric (PG&E: 4147571902-1 / 4149482340) Usage | there are import and export electric meters, what are they. This electric meter is negative | 0.9226 | 2.6344
2023-02-01 | Simpkins Athletics Building | 22495 | Athletics |  | 2272.571 | 887.7258 | [9 empty] | Simpkins Athletic: Gas (PG&E: 4147571902-1 / 3037101005) Usage |  | 0.082802 | 3.172
2023-03-01 | Simpkins Athletics Building | 22495 | Athletics |  | 1530.2784 | 775.3411 | [11 empty] | 0.084483 | 2.0638
2023-04-01 | Simpkins Athletics Building | 22495 | Athletics |  | -428.1347 | 397.4331 | [11 empty] | 0.080837 | 0.78849
2023-05-01 | Simpkins Athletics Building | 22495 | Athletics |  | -2094.6438 | 156.2333 | [11 empty] | 0.082393 | 0.28206
2023-06-01 | Simpkins Athletics Building | 22495 | Athletics |  | -2325.0182 | 39.5848 | [11 empty] | 0.078697 | 0.10278
2023-07-01 | Simpkins Athletics Building | 22495 | Athletics |  | -1613.906 | 8.1818 | [11 empty] | 0.082689 | 0.052619
2023-08-01 | Simpkins Athletics Building | 22495 | Athletics |  | 2218.7241 | 0 | [11 empty] | 0.088851 | 0.039902
2023-09-01 | Simpkins Athletics Building | 22495 | Athletics |  | 3322 | 0 | [11 empty] | 0.087258 | 0.039907
2023-10-01 | Simpkins Athletics Building | 22495 | Athletics |  | 3581.1793 | 42.4218 | [11 empty] | 0.090475 | 0.135
2023-11-01 | Simpkins Athletics Building | 22495 | Athletics |  | 3992.0465 | 260.6427 | [11 empty] | 0.088973 | 0.71804
2023-12-01 | Simpkins Athletics Building | 22495 | Athletics |  | 4060.1935 | 514.0323 | [11 empty] | 7.3346 | 1.4489
2023-01-01 | Simpkins Center Storage Building | 768 | Storage | 88.7446 | [5 empty] | 4.5741 | 0 | 0 | 0 |  | 4.5741 | Storage Electric (PG&E: 4147571902-1 / 4145273835) Usage |  | 0.034181
2023-02-01 | Simpkins Center Storage Building | 768 | Storage | 86.9948 | [13 empty] | 0.036142
2023-03-01 | Simpkins Center Storage Building | 768 | Storage | 90.2683 | [13 empty] | 0.035933
2023-04-01 | Simpkins Center Storage Building | 768 | Storage | 91.3033 | [13 empty] | 0.037231
2023-05-01 | Simpkins Center Storage Building | 768 | Storage | 82.4039 | [13 empty] | 0.034484
2023-06-01 | Simpkins Center Storage Building | 768 | Storage | 71.0507 | [13 empty] | 0.033174
2023-07-01 | Simpkins Center Storage Building | 768 | Storage | 77.2261 | [13 empty] | 0.035826
2023-08-01 | Simpkins Center Storage Building | 768 | Storage | 97.502 | [13 empty] | 0.042387
2023-09-01 | Simpkins Center Storage Building | 768 | Storage | 84.0416 | [13 empty] | -0.00076806
2023-10-01 | Simpkins Center Storage Building | 768 | Storage | 93.6376 | [13 empty] | 0.026848
2023-11-01 | Simpkins Center Storage Building | 768 | Storage | 85.697 | [13 empty] | 0.0379
2023-12-01 | Simpkins Center Storage Building | 768 | Storage | 80.6954 | [13 empty] | 0.036983
2023-01-01 | Simpkins Stadium Center | 22203 | Office | 11411.5008 | 9681.4462 | 1373.0875 |  |  |  | 32.4801 | 51.8486 | 0 | 0 |  | 84.3287 | SC: Simpkins Stadium PG&E SMD: Simpkins Ctr Electric (4147571902 / 1887205009) Usage | there are two electric meters, one has negative, why are they different meters with the similar account number | 2.4522 | 4.5653
2023-02-01 | Simpkins Stadium Center | 22203 | Office | 17032.1599 | 7760.2538 | 1383.2847 | [9 empty] | Simpkins Ctr: Gas (PG&E: 4147571902-1 / 9537109005) Usage |  | 2.4509 | 4.8972
2023-03-01 | Simpkins Stadium Center | 22203 | Office | 19036.56 | 5797.6873 | 1423.5278 | [9 empty] | Simpkins Ctr: Electric (PG&E: 4147571902-1 / 4149271279) Usage |  | 2.4366 | 3.6177
2023-04-01 | Simpkins Stadium Center | 22203 | Office | 20529.3599 | 270.696 | 1145.5 | [11 empty] | 2.6009 | 2.2727
2023-05-01 | Simpkins Stadium Center | 22203 | Office | 16810.08 | -6779.3468 | 719.3333 | [11 empty] | 1.6629 | 1.178
2023-06-01 | Simpkins Stadium Center | 22203 | Office | 19275.3599 | -8725.0907 | 532.8788 | [11 empty] | 1.7645 | 0.93961
2023-07-01 | Simpkins Stadium Center | 22203 | Office | 23554.5599 | -6518.4332 | 572.1327 | [11 empty] | 2.7221 | 1.0109
2023-08-01 | Simpkins Stadium Center | 22203 | Office | 23375.4399 | 10660.4207 | 565.3218 | [11 empty] | 4.0325 | 1.0578
2023-09-01 | Simpkins Stadium Center | 22203 | Office | 17492.72 | 13857.7 | 584.3333 | [11 empty] | 3.8613 | 1.2461
2023-10-01 | Simpkins Stadium Center | 22203 | Office | 16562.16 | 13000.6205 | 901.2482 | [11 empty] | 3.3598 | 2.0696
2023-11-01 | Simpkins Stadium Center | 22203 | Office | 13332.16 | 12438.9117 | 1164.0851 | [11 empty] | 2.9859 | 3.0294
2023-12-01 | Simpkins Stadium Center | 22203 | Office | 12946.48 | 11245.7097 | 1147.2121 | [11 empty] | 2.5095 | 3.1838
2023-01-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 88851.5909 |  |  | 31587.0975 | 3801.0383 |  | 19.0394 | 0 | 170.4739 | 19.7817 |  | 209.2951 | SRAC Electric (M) Usage | [87 empty] | 3801.0383
2023-02-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 74720.75 |  |  | 29049.4531 | 3699.7728 | [7 empty] | SRAC Steam (M) Usage | [87 empty] | 3699.7728
2023-03-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 64608.1239 |  |  | 28763.7309 | 3075.859 | [7 empty] | SRAC CHW (M) Usage | [87 empty] | 3075.859
2023-04-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 35142.1261 |  |  | 17941.7378 | 7878.091 | [95 empty] | 7878.091
2023-05-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 38198.5 |  |  | 13205.0781 | 14006.4395 | [95 empty] | 14006.4395
2023-06-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 22262.3571 |  |  | 8201.25 | 21896.1627 | [95 empty] | 21896.1627
2023-07-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 22687.1429 |  |  | 4881.6406 | 35118.4572 | [95 empty] | 35118.4572
2023-08-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 43866.55 |  |  | 4396.6719 | 45108.4003 | [95 empty] | 45108.4003
2023-09-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 51883.325 |  |  | 8376.9609 | 27645.9801 | [95 empty] | 27645.9801
2023-10-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 70783.625 |  |  | 11863.3984 | 24451.6761 | [95 empty] | 24451.6761
2023-11-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 76702.3985 |  |  | 20983.1145 | 7379.6066 | [95 empty] | 7379.6066
2023-12-01 | Spartan Recreation and Aquatic Center | 121426 | Athletics | 87867.5325 |  |  | 27749.496 | 6106.7352 | [95 empty] | 6106.7352
2018-01-01 | SPX Central | 86252 | Athletics | 43042.75 |  | 217 | 747.7393 | 414.8324 |  | 23.9984 | 0.54854 | 7.8499 | 6.5648 |  | 38.9617 | SPXWest: Electric (M) Usage - Archived | Are SPX central and west different ? All meters are labeled as west(archived) and submeters are central. Which should we take |  | 0.35898
2018-02-01 | SPX Central | 86252 | Athletics | 53340 |  | 152 | 1518.3801 | 1455.2587 | [7 empty] | SPX/YUH Gas (PG&E: 4880418295-3 / 4880418005) Usage |  |  | 0.28667
2018-03-01 | SPX Central | 86252 | Athletics | 54715.875 |  | 81 | 1607.8101 | 1825.9295 | [7 empty] | SPXWest: Steam (M) Usage - Archived |  |  | 0.13855
2018-04-01 | SPX Central | 86252 | Athletics | 52914.75 |  | 1.6216 | 797.1301 | 2341.5618 | [7 empty] | SPXWest: Chilled Water (M) Usage - Archived |  |  | 0.021059
2018-05-01 | SPX Central | 86252 | Athletics | 49630 |  | 1.9784 | 374.5203 | 3097.9323 | [10 empty] | 0.023583
2018-06-01 | SPX Central | 86252 | Athletics | 48220.75 |  | 2 | 73.02 | 5839.328 | [10 empty] | 0.024242
2018-07-01 | SPX Central | 86252 | Athletics | 47051 |  | 2.0129 | 50 | 9496.2 | [10 empty] | 0.024242
2018-08-01 | SPX Central | 86252 | Athletics | 50924 |  | 2.8065 | 100 | 8163.4 | [10 empty] | 0.025407
2018-09-01 | SPX Central | 86252 | Athletics | 52806 |  | 2.2358 | 100 | 6330.8 | [10 empty] | 0.024723
2018-10-01 | SPX Central | 86252 | Athletics | 58148 |  | 1.9677 | 170 | 6164.2 | [10 empty] | 0.024366
2018-11-01 | SPX Central | 86252 | Athletics | 53666 |  | 4.3771 | 550 | 1749.3 | [10 empty] | 0.028785
2018-12-01 | SPX Central | 86252 | Athletics | 42197.2809 |  | 4.125 | 682.1178 | 307.1374 | [10 empty] | 0.028574
2023-01-01 | SPX East | 29240 | Athletics |  |  |  | 2124.1827 |  |  | 0 | 0 | 47.4192 | 0 |  | 47.4192 | SPX East: Steam (east) (M) Usage | Electric demand is 0 | [89 empty] | 210.5352
2023-02-01 | SPX East | 29240 | Athletics |  |  |  | 2170.7031 | [99 empty] | 213.0703
2023-03-01 | SPX East | 29240 | Athletics |  |  |  | 2036.0253 | [99 empty] | 198.5967
2023-04-01 | SPX East | 29240 | Athletics |  |  |  | 1261.0352 | [99 empty] | 127.2646
2023-05-01 | SPX East | 29240 | Athletics |  |  |  | 927.2461 | [99 empty] | 92.9375
2023-06-01 | SPX East | 29240 | Athletics |  |  |  | 811.7076 | [99 empty] | 80.7979
2023-07-01 | SPX East | 29240 | Athletics |  |  |  | 719.7084 | [99 empty] | 68.5117
2023-08-01 | SPX East | 29240 | Athletics |  |  |  | 308.2677 | [99 empty] | 32.4844
2023-09-01 | SPX East | 29240 | Athletics |  |  |  | 268.3169 | [99 empty] | 24.3809
2023-10-01 | SPX East | 29240 | Athletics |  |  |  | 543.2397 | [99 empty] | 49.3945
2023-11-01 | SPX East | 29240 | Athletics |  |  |  | 1162.3625 | [99 empty] | 112.1924
2023-12-01 | SPX East | 29240 | Athletics |  |  |  | 1532.5756 | [99 empty] | 153.9883
2019-01-01 | Storage Building | 3135 | Storage | 3598.6235 | [5 empty] | 54.7495 | 0 | 0 | 0 |  | 54.7495 | Housing: Block House Electric (Closed) (PG&E: 4147571902-1 / 8368689835) Usage |  | 1.1273
2019-02-01 | Storage Building | 3135 | Storage | 3539.8026 | [13 empty] | 1.238
2019-03-01 | Storage Building | 3135 | Storage | 3992.5255 | [13 empty] | 1.2656
2019-04-01 | Storage Building | 3135 | Storage | 3691.6479 | [13 empty] | 1.2506
2019-05-01 | Storage Building | 3135 | Storage | 3528.6717 | [13 empty] | 1.1952
2019-06-01 | Storage Building | 3135 | Storage | 3535.9463 | [13 empty] | 1.2527
2019-07-01 | Storage Building | 3135 | Storage | 4422.4287 | [13 empty] | 1.5192
2019-08-01 | Storage Building | 3135 | Storage | 5257.2763 | [13 empty] | 1.7902
2019-09-01 | Storage Building | 3135 | Storage | 5656.3381 | [13 empty] | 1.9926
2019-10-01 | Storage Building | 3135 | Storage | 5177.9971 | [13 empty] | 1.7622
2019-11-01 | Storage Building | 3135 | Storage | 4257.6198 | [13 empty] | 1.4125
2019-12-01 | Storage Building | 3135 | Storage | 3645.878 | [13 empty] | 1.1615
2023-01-01 | Student Services Center | 99853 | Office | 92265.6364 |  | 2307.4572 |  |  |  | 46.8056 | 17.3045 | 0 | 0 |  | 64.1101 | SSC: Main Electric (M) Usage | should we be adding ramp lighing electric |  | 7.5795 | [88 empty] | 29968.9394
2023-02-01 | Student Services Center | 99853 | Office | 90699 |  | 2079.6054 | [9 empty] | SSC: Gas (PG&E: 9817802206-1 / 9817802005) Usage |  |  | 7.3111 | [88 empty] | 26566
2023-03-01 | Student Services Center | 99853 | Office | 99974.83 |  | 2749.1833 | [12 empty] | 6.7166 | [88 empty] | 28881.6593
2023-04-01 | Student Services Center | 99853 | Office | 108658.67 |  | 2273.4028 | [12 empty] | 4.53 | [88 empty] | 27422.3407
2023-05-01 | Student Services Center | 99853 | Office | 126200 |  | 1283.5771 | [12 empty] | 2.049 | [88 empty] | 29196
2023-06-01 | Student Services Center | 99853 | Office | 119129.0854 |  | 974.2389 | [12 empty] | 1.6571 | [88 empty] | 26113.1707
2023-07-01 | Student Services Center | 99853 | Office | 141154.9146 |  | 1033.4063 | [12 empty] | 1.7741 | [88 empty] | 27376.0793
2023-08-01 | Student Services Center | 99853 | Office | 146382.8857 |  | 990.6207 | [12 empty] | 1.792 | [88 empty] | 27874.5357
2023-09-01 | Student Services Center | 99853 | Office | 122037.818 |  | 470.6696 | [12 empty] | 0.97337 | [88 empty] | 27802.955
2023-10-01 | Student Services Center | 99853 | Office | 121262.7963 |  | 338.8273 | [12 empty] | 0.82228 | [88 empty] | 29214.2593
2023-11-01 | Student Services Center | 99853 | Office | 103366.6696 |  | 1159.8178 | [12 empty] | 3.0995 | [88 empty] | 28890.2336
2023-12-01 | Student Services Center | 99853 | Office | 98644.9511 |  | 1618.2645 | [12 empty] | 4.4594 | [88 empty] | 29973.8095
2023-01-01 | Student Wellness Center | 52700 | Office | 16215.2955 |  |  | 2273.7743 | 1904.5964 |  | 11.0861 | 0 | 27.6867 | 8.9511 |  | 47.724 | SWC: Electric (M) Usage | [93 empty] | 1904.5964
2023-02-01 | Student Wellness Center | 52700 | Office | 14668 |  |  | 2212.6563 | 1514.49 | [7 empty] | SWC: Steam (M) Usage | [93 empty] | 1514.49
2023-03-01 | Student Wellness Center | 52700 | Office | 14941.9554 |  |  | 1924.0319 | 2649.9044 | [7 empty] | SWC: CHW (M) Usage | [93 empty] | 2649.9044
2023-04-01 | Student Wellness Center | 52700 | Office | 12311.1696 |  |  | 1179.386 | 3497.294 | [101 empty] | 3497.294
2023-05-01 | Student Wellness Center | 52700 | Office | 13012.125 |  |  | 878.7305 | 4064.7797 | [101 empty] | 4064.7797
2023-06-01 | Student Wellness Center | 52700 | Office | 10883.5976 |  |  | 550.2596 | 3816.7725 | [101 empty] | 3816.7725
2023-07-01 | Student Wellness Center | 52700 | Office | 11242.5572 |  |  | 559.3977 | 4324.009 | [101 empty] | 4324.009
2023-08-01 | Student Wellness Center | 52700 | Office | 13090.9776 |  |  | 432.2775 | 4472.7492 | [101 empty] | 4472.7492
2023-09-01 | Student Wellness Center | 52700 | Office | 14713.4837 |  |  | 513.4719 | 3924.0323 | [101 empty] | 3924.0323
2023-10-01 | Student Wellness Center | 52700 | Office | 16622.7589 |  |  | 753.3824 | 3918.444 | [101 empty] | 3918.444
2023-11-01 | Student Wellness Center | 52700 | Office | 16182.0404 |  |  | 1357.0958 | 2947.967 | [101 empty] | 2947.967
2023-12-01 | Student Wellness Center | 52700 | Office | 17346.593 |  |  | 1956.4328 | 2275.2955 | [101 empty] | 2275.2955
2023-01-01 | Sweeney Hall | 101932 | Academic | 27602.2586 |  |  | 0.0048865 | 523.9024 |  | 8.4358 | 0 | 2.8797e-05 | 6.462 |  | 14.8978 | Sweeney Hall: Electricity (M) Usage | elec rm 122 meter not considered(not there in 2023) | [96 empty] | 0.48865 |  | 36.5426 | 5.8999
2023-02-01 | Sweeney Hall | 101932 | Academic | 26236 |  |  | 0.0053778 | 759.3894 | [7 empty] | SH: Steam Rm 122 Usage (M) | steam N4 meter is 0,no other steam meter availble | [96 empty] | 0.53778 |  | 123.164 | 6.4758
2023-03-01 | Sweeney Hall | 101932 | Academic | 23054.1346 |  |  | 0.0041872 | 254.694 | [105 empty] | 0.41872 |  | 207.9708
2023-04-01 | Sweeney Hall | 101932 | Academic | 16784.3654 |  |  | 0.002323 | 2504.3509 | [7 empty] | Sweeney Hall: Chilled Water 1 (M) Usage | chilled water 1 and 2 added . CHW rm 122/128 not considered - do we need to? | [96 empty] | 0.2323 |  | 1590.0326 | 14.1074
2023-05-01 | Sweeney Hall | 101932 | Academic | 16474.5 |  |  | 0.0016025 | 2958.2964 | [7 empty] | Sweeney Hall: Chilled Water 2 (M) Usage | [97 empty] | 0.16025 |  | 1994.7526 | 8.0615
2023-06-01 | Sweeney Hall | 101932 | Academic | 11786.5714 |  |  | 0.0010865 | 5871.6262 | [105 empty] | 0.10865 |  | 3498.1511 | 23.6772
2023-07-01 | Sweeney Hall | 101932 | Academic | 10331.9286 |  |  | 0.00053681 | 11047.6189 | [105 empty] | 0.053681 |  | 5508.1618 | 64.1299
2023-08-01 | Sweeney Hall | 101932 | Academic | 13404.8429 |  |  | 0.00042746 | 11687.476 | [105 empty] | 0.042746 |  | 4254.1308 | 73.4175
2023-09-01 | Sweeney Hall | 101932 | Academic | 21855.05 |  |  | 0.00078687 | 10794.6133 | [105 empty] | 0.078687 |  | 4088.4281 | 82.2705
2023-10-01 | Sweeney Hall | 101932 | Academic | 27285.1071 |  |  | 0.0016036 | 7115.8275 | [105 empty] | 0.16036 |  | 3185.3206 | 39.7998
2023-11-01 | Sweeney Hall | 101932 | Academic | 28718.6211 |  |  | 0.0031886 | 1189.7701 | [105 empty] | 0.31886 |  | 732.8549 | 11.437
2023-12-01 | Sweeney Hall | 101932 | Academic | 28482.0858 |  |  | 0.0033459 | 182.7883 | [105 empty] | 0.33459 |  | 137.1602
2023-01-01 | Washburn Hall (Student Residence) | 39332 | Residential | 14832.8815 |  |  | 2117.7581 |  |  | 20.7689 | 0 | 39.4928 | 0 |  | 60.2617 | WSH: Elec (PG&E: 9340746607-2 / 9341926972) Usage |  |  | 6.9976 | [100 empty] | 5.8958 | 14832.8815 | 2117.7581
2023-02-01 | Washburn Hall (Student Residence) | 39332 | Residential | 19052.7331 |  |  | 2476.5484 | [8 empty] | WSH: NatGas (PG&E: 4564269832-3 / 4564269015) Usage |  |  | 8.8052 | [100 empty] | 7.7117 | 19052.7331 | 2476.5484
2023-03-01 | Washburn Hall (Student Residence) | 39332 | Residential | 20003.2768 |  |  | 2426.3977 | [11 empty] | 6.3735 | [100 empty] | 7.3885 | 20003.2768 | 2426.3977
2023-04-01 | Washburn Hall (Student Residence) | 39332 | Residential | 19028.3371 |  |  | 1837.8896 | [11 empty] | 3.3527 | [100 empty] | 8.0186 | 19028.3371 | 1837.8896
2023-05-01 | Washburn Hall (Student Residence) | 39332 | Residential | 17401.797 |  |  | 1365.7127 | [11 empty] | 2.1655 | [100 empty] | 7.3522 | 17401.797 | 1365.7127
2023-06-01 | Washburn Hall (Student Residence) | 39332 | Residential | 11922.8375 |  |  | 662.2935 | [11 empty] | 1.1387 | [100 empty] | 5.3058 | 11922.8375 | 662.2935
2023-07-01 | Washburn Hall (Student Residence) | 39332 | Residential | 14108.9892 |  |  | 244.6419 | [11 empty] | 0.46887 | [100 empty] | 6.8042 | 14108.9892 | 244.6419
2023-08-01 | Washburn Hall (Student Residence) | 39332 | Residential | 27071.464 |  |  | 282.6774 | [11 empty] | 0.56259 | [100 empty] | 12.2074 | 27071.464 | 282.6774
2023-09-01 | Washburn Hall (Student Residence) | 39332 | Residential | 32593.7637 |  |  | 420.5462 | [11 empty] | 0.91522 | [100 empty] | 14.2447 | 32593.7637 | 420.5462
2023-10-01 | Washburn Hall (Student Residence) | 39332 | Residential | 28446.4133 |  |  | 810.2291 | [11 empty] | 1.8528 | [100 empty] | 11.7463 | 28446.4133 | 810.2291
2023-11-01 | Washburn Hall (Student Residence) | 39332 | Residential | 19776.7044 |  |  | 1414.0634 | [11 empty] | 3.7051 | [100 empty] | 8.2804 | 19776.7044 | 1414.0634
2023-12-01 | Washburn Hall (Student Residence) | 39332 | Residential | 15175.8854 |  |  | 1474.5419 | [11 empty] | 4.0667 | [100 empty] | 6.2843 | 15175.8854 | 1474.5419
2023-01-01 | Washington Square Hall | 71857 | Academic | 46348.2676 |  |  | 3364.5566 | 2042.4901 |  | 45.6115 | 0 | 33.9486 | 23.9282 |  | 103.4883 | Washington Square Hall : Electricity (M) Usage
2023-02-01 | Washington Square Hall | 71857 | Academic | 71099.9966 |  |  | 2587.87 | 855.366 | [7 empty] | Washington Square Hall : Steam (M) Usage
2023-03-01 | Washington Square Hall | 71857 | Academic | 80123.738 |  |  | 2694.7229 | 616.2 | [7 empty] | Washington Square Hall : Chilled Water (M) Usage
2023-04-01 | Washington Square Hall | 71857 | Academic | 82076.2361 |  |  | 2013.2071 | 4007.1791
2023-05-01 | Washington Square Hall | 71857 | Academic | 87100.029 |  |  | 1764.64 | 9035.2178
2023-06-01 | Washington Square Hall | 71857 | Academic | 83853.6169 |  |  | 1154.422 | 10410.1026
2023-07-01 | Washington Square Hall | 71857 | Academic | 87146.3869 |  |  | 722.353 | 11966.0684
2023-08-01 | Washington Square Hall | 71857 | Academic | 87597.0023 |  |  | 11.5896 | 19501.0131
2023-09-01 | Washington Square Hall | 71857 | Academic | 90265.8185 |  |  | 354.2384 | 19965.4285
2023-10-01 | Washington Square Hall | 71857 | Academic | 91037.0968 |  |  | 1386.052 | 21697.2081
2023-11-01 | Washington Square Hall | 71857 | Academic | 77191.4623 |  |  | 3952.953 | 20964.2175
2023-12-01 | Washington Square Hall | 71857 | Academic | 76742.9836 |  |  | 4387.8367 | 22223.4934
2023-01-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 28571.1638 |  |  | 1867.6502 |  |  | 13.8086 | 0 | 11.3418 | 7.6799 |  | 32.8302 | Uchida Hall: Electricity (M) Usage | 2018 CHW data considered cause 2023 data quality is poor | [109 empty] | 0 |  | 190.4023
2023-02-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 25835.5 |  |  | 1639.2969 | 1209.5176 | [7 empty] | Uchida Hall: Steam (M) Usage | [110 empty] | 0 |  | 160.4805
2023-03-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 27316.0521 |  |  | 806.5195 | 1958.3838 | [7 empty] | YUH: CHW (M) Usage - Archived | [110 empty] | 0 |  | 84.7998
2023-04-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 23452.1979 |  |  | 453.6758 | 2748.0662 | [118 empty] | 0 |  | 41.4355
2023-05-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 22303.5 |  |  | 402.9004 | 4181.6559 | [118 empty] | 0 |  | 40.5928
2023-06-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 19456.0714 |  |  | 158.3873 | 5997.6 | [118 empty] | 0 |  | 17.0625
2023-07-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 20295.4286 |  |  | 107.3744 | 9163 | [118 empty] | 0.00097656 |  | 9.0371
2023-08-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 24113.35 |  |  | 60.1317 | 7830.2 | [118 empty] | 7.6008 |  | 5.3262
2023-09-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 26067.2333 |  |  | 97.5665 | 7497 | [118 empty] | 0 |  | 9.5469
2023-10-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 29862.6667 |  |  | 100.9834 | 5997.6 | [118 empty] | 0 |  | 9.8047
2023-11-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 30724.3285 |  |  | 1069.6306 | 1999.2 | [118 empty] | 0 |  | 98.166
2023-12-01 | Yoshihiro Uchida Hall | 76871 | Athletics | 33103.9646 |  |  | 1954.4602 | 614.2747 | [118 empty] | 0 |  | 198.9971
Note on D375: Marya Thawer: Could be residential

## Archived - Annual EUIs
Row Labels | Average of Electric EUI(kBtu/sq.ft) | Average of Gas EUI(kBtu/sq.ft) | Average of Chilled Water EUI(kBtu/sq.ft) | Average of Steam EUI(kBtu/sq.ft)
Academic | 24.9598 | 0.91063 | 17.1507 | 100.2528
Art | 34.3445 | 0.0061174 | 20.7447 | 47.2631
Boccardo Business Classroom Building | 45.4589 |  | 34.8871 | 86.1736
Central Classroom Building | 31.0078 | 0.80856 | 41.7191 | 29.6447
Child Development Center | 10.0648 | 7.1905
Clark Hall | 16.6365 |  | 12.771 | 37.487
Dwight Bentel Hall | 19.0632 | 0 | 3.1597 | 40.781
Engineering | 36.3857 | 0 | 36.9791 | 35.7775
Health Building | 28.4308 | 0 | 34.7958 | 36.5378
Hugh Gillis Hall | 27.0313 | 0 | 16.2501 | 957.2377
MacQuarrie Hall | 36.466 | 0 | 8.4125 | 17.9083
MacQuarrie Hall- Spartan Shops
Music | 7.7123 | 0 | 0.00012193 | 80.7805
Reid Hillview Airport | 5.8976 | 3.833 | 0 | 0
Science | 21.8512 | 0 | 0 | 0
Sweeney Hall | 8.4358 | 0 | 6.462 | 2.8797e-05
Washington Square Hall | 45.6115 | 0 | 23.9282 | 33.9486
Athletics | 22.7636 | 11.7565 | 4.2614 | 37.9563
Field House | 35.1067 | 32.9273 | 0 | 0
Koret Center | 27.0313 | 43.3358 | 0 | 0
Provident Credit Union Event Center | 63.1248 | 0 | 0.064578 | 66.5652
Simpkins Athletics Building | 0 | 17.2407 | 0 | 0
Spartan Recreation and Aquatic Center | 19.0394 | 0 | 19.7817 | 170.4739
SPX Central | 23.9984 | 0.54854 | 6.5648 | 7.8499
SPX East | 0 | 0 | 0 | 47.4192
Yoshihiro Uchida Hall | 13.8086 | 0 | 7.6799 | 11.3418
Food Service | 129.8267 | 155.3999
Dining Commons | 129.8267 | 155.3999
Lab | 34.5792 | 20.3708 | 20.4673 | 28.6521
Duncan Hall | 30.927 | 0.075595 | 23.7307 | 69.7543
Industrial Studies | 11.9823 | 12.4819 | 0 | 2.6921
Interdisciplinary Science Building | 45.1251 | 0 | 58.1387 | 42.1622
Moss Landing Marine Lab Main Laboratory | 50.2825 | 68.9258 | 0 | 0
Library | 0.026555 | 0 | 29.274 | 13.668
Dr. Martin Luther King, Jr. Library | 0.026555 | 0 | 29.274 | 13.668
Dr. Martin Luther King, Jr. Library-Tenants
Office | 27.4053 | 24.8629 | 2.2378 | 6.9217
Administration | 0
Associated Students House | 15.3777
Automated Bank Teller Facility | 70.9973
Business Tower
Corporation Yard Offices |  | 21.7167
International House | 15.0903 | 33.4447 | 0 | 0
Simpkins Stadium Center | 32.4801 | 51.8486 | 0 | 0
Student Services Center | 46.8056 | 17.3045 | 0 | 0
Student Wellness Center | 11.0861 | 0 | 8.9511 | 27.6867
Outdoor Athletics | 141.1098
CEFCU Stadium | 141.1098
Outdoor Physical Education
Residential | 20.7764 | 0 | 7.963 | 41.7769
Campus Village Phase 2 | 20.7839 |  | 15.9259 | 44.0611
Joe West Hall
Washburn Hall (Student Residence) | 20.7689 | 0 | 0 | 39.4928
Storage | 27.6995 | 15.7799 | 0 | 0
Art Foundry | 23.7748 | 47.3396
Concession Buildings
Simpkins Center Storage Building | 4.5741 | 0 | 0 | 0
Storage Building | 54.7495 | 0 | 0 | 0
Theater | 68.1435 | 18.5483 | 0 | 0
Hammer Theater | 68.1435 | 18.5483 | 0 | 0
Warehouse
Corporation Yard Trades Building
(blank) | #DIV/0! | 0 | 5.1972 | 11.9445
Campus Village 1 | 2.173 |  | 10.3943 | 23.889
Campus Village A-Food Tenant | #DIV/0!
Golf Complex
Modular F,A,B | 39.7241 | 0 | 0 | 0
Outdoor Physical Education-2
SC_Track & Field
Grand Total | #DIV/0! | 14.0257 | 11.0688 | 51.8578
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.